## 1. 220 kV AIS
Technical Data Sheets
BIDDER’S / CONTRACTOR’S GUARANTEED DATA |  | Unit | Data required | Data offered
No. | Description
1 | 220 kV Air Insulated Switchgear (AIS)
1.1 | 220 kV Capacitive Voltage Transformer
1.1.1 | Manufacturer | - | -
1.1.2 | Place of manufacture | - | -
1.1.3 | Model designation | - | -
1.1.4 | Applicable standard | - | IEC 60071-1
IEC 60071-2
IEC 61869-1
IEC 61869-5
IEC 60358-1
IEC 60529
IEC 60815
1.1.5 | Type | - | outdoor, capacitor type
1.1.6 | Highest voltage for equipment Um | kV | 245
1.1.7 | Rated primary voltage | kV | 220 / √3
1.1.8 | Number of secondary windings |  | 3
1.1.9 | · for protection | - | combined
1.1.10 | · for measurement | - | combined
1.1.11 | · for metering | - | 1
1.1.12 | Rated secondary voltage:
1.1.13 | · protection winding | V | 110 / √3
1.1.14 | · measurement winding | V | 110 / √3
1.1.15 | · metering winding | V | 110 / √3
1.1.16 | Accuracy class for protection | - | 3P
1.1.17 | Accuracy class for measurement | - | 0.5
1.1.18 | Accuracy class for metering | - | 0.2S
1.1.19 | Total rated burden secondary windings | VA | 3 x 50
1.1.20 | Type of insulators | - | silicon
1.1.21 | Minimum Unified Specific Creepage Distance (USCD) | mm/kV | 43.3
1.1.22 | Rated lightning impulse withstand voltage | kVpeak | 1050
1.1.23 | Rated power frequency withstand voltage | kVrms | 460
1.1.24 | Tests according to VII-5 Technical Specification | yes/no | yes
1.2 | 220 kV Lightning Arrester and Discharge Counter
1.2.1 | Manufacturer | - | -
1.2.2 | Place of manufacture | - | -
1.2.3 | Model designation | - | -
1.2.4 | Applicable standard | - | IEC 60071-1
IEC 60071-2
IEC 60099-4
IEC 60099-5
IEC 60529
IEC 60815
1.2.5 | Type | - | Outdoor, silicon-housed
1.2.6 | System data:
1.2.7 | · Nominal system voltage | kV | 220
1.2.8 | · Highest system voltage | kV | 245
1.2.9 | · System frequency | Hz | 50
1.2.10 | Rated voltage Ur | kV | 180
1.2.11 | Maximum continuous operating voltage Uc | kV | 144
1.2.12 | Rated discharge current | kA | 10 / 20 subject to calculation
1.2.13 | Thermal energy rating | kJ/kV | 10
1.2.14 | Separate earthing rod per SA, 150 mm2 | yes/no | yes
1.2.15 | Discharge Counter:
1.2.16 | Manufacturer | -
1.2.17 | Model designation | -
1.2.18 | Display | -
1.2.19 | Number of impulses | yes/no | yes
1.2.20 | Leakage current measurement, total current | yes/no | yes
1.2.21 | Protection class | - | IP55 W
1.2.22 | Number of counters per three (3) 1-ph arresters | - | 3
1.2.23 | Tests according to VII-5 Technical Specification | yes/no | yes
1.3 | 220 kV Post Insulator
1.3.1 | Manufacturer | -
1.3.2 | Place of manufacture | -
1.3.3 | Type | - | outdoor, silicon
1.3.4 | Applicable standard | - | IEC 60071-1
IEC 60071-2
IEC 60168
IEC 60273
IEC 60815
IEC 61952
IEC 62217
IEC 62231-1
IEC 61462
IEC 62772
1.3.5 | Model designation | -
1.3.6 | IEC post insulator designation | -
1.3.7 | System nominal voltage | kV | 220
1.3.8 | Highest voltage of equipment | kV | 245
1.3.9 | Rated lightning impulse withstand voltage, dry | kVpeak | 1050
1.3.10 | Rated switching impulse withstand voltage, wet | kVpeak | 460
1.3.11 | Minimum Unified Specific Creepage Distance (USCD) | mm/kV | 43.3
1.3.12 | Minimum failing load, bending | kN
1.3.13 | Tests according to VII-5 Technical Specification | yes/no | yes
1.4 | 220 kV Insulator String
1.4.1 | Insulator units
1.4.2 | Applicable standard | - | IEC 60071-1
IEC 60071-2
IEC 60120
IEC 60383-1
IEC 60383-2
IEC 60305
IEC 60372
IEC 60815
IEC 61109
IEC 61466
1.4.3 | Manufacturer | -
1.4.4 | Type | -
1.4.5 | Insulating body material | - | silicon
1.4.6 | Rated electromechanical or mechanical strength | kN
1.4.7 | Max. shed diameter | mm
1.4.8 | Minimum Unified Specific Creepage Distance (USCD) | mm/kV | 43.3
1.4.9 | Tests according to VII-5 Technical Specification | yes/no | yes
1.5 | 220 kV Insulator String
1.5.1 | Manufacturer | -
1.5.2 | Place of manufacture | -
1.5.3 | Type | -
1.5.4 | Insulating body material | - | silicon
1.5.5 | Applicable standard | - | IEC 60071-1, IEC 60071-2 IEC 60120, IEC 60383-1, IEC 60383-2, IEC 60305, IEC 60372, IEC 60815, IEC 61109, IEC 61466
1.5.6 | Rated electromechanical or mechanical strength | kN
1.5.7 | Max. shed diameter | mm
1.5.8 | Minimum Unified Specific Creepage Distance (USCD) | mm/kV | 43.3
1.5.9 | Tests according to VII-5 Technical Specification | yes/no | yes
1.6 | 220 kV Tubular Busbar
1.6.1 | Applicable standard | - | DIN 43670
DIN 46276-1
EN 755-1
EN 755-2
EN 755-7
1.6.2 | Manufacturer | -
1.6.3 | Place of manufacture | -
1.6.4 | Type | -
1.6.5 | Type for road crossings or other special purposes | -
1.6.6 | Rated current | A | 4000
1.6.7 | Rated short time current (3s) | kA | ≥ 40
1.6.8 | Cross-section | mm2 | -
1.6.9 | Tubular type: | - | Aluminum
1.6.11 | Overall diameter | mm | ≥250
1.6.12 | Internal diameter | mm | -
1.6.13 | Tube weight | kg/m | -
1.6.14 | Theoretical breaking force | kN | -
1.6.15 | Ohmic resistance at 20°C | Ω/km | -
1.6.16 | Tests according to VII-5 Technical Specification | yes/no | yes
1.7 | 220 kV Conductor
1.7.1 | Applicable standard | - | IEC 60104
IEC 61089
IEC 61232
IEC 62004
1.7.2 | Manufacturer | - | -
1.7.3 | Place of manufacture | - | -
1.7.4 | Type | - | -
1.7.5 | Rated current | A | -
1.7.6 | Rated short time current (3s) | kA | ≥ 40
1.7.7 | Total cross-section | mm2 | -
1.7.8 | Number of strands x diameter: |  | -
1.7.9 | Aluminum | #/mm | -
1.7.10 | Steel | #/mm | -
1.7.11 | Overall diameter | mm | -
1.7.12 | Conductor weight | kg/m | -
1.7.13 | Theoretical breaking force | kN | -
1.7.14 | Ohmic resistance at 20°C | Ω/km | -
1.7.15 | Tests according to VII-5 Technical Specification | yes/no | yes
1.8 | 220 kV Clamps/dead-end joints (to be filled in separately for each type)
1.8.1 | Manufacturers | -
| Type | -
| Cross-section | mm2
| Rated current | A | 4000
1.8.2 | Busbar | A | 4000
1.8.3 | Connections | A | 4000
1.8.4 | Tests according to VII-5 Technical Specification | yes/no | yes
1.9 | Steel Structures
1.9.1 | Manufacturer | -
| Place of manufacture | -
| Applicable standard | -
| Material | -
1.9.2 | Factor of safety in calculation | -
1.9.3 | Galvanization thickness:
1.9.4 | Steel sections thicker than 5 mm | μm
1.9.5 | Steel sections 2 mm-5 mm | μm
1.9.6 | Bolts and nuts | μm
1.9.7 | Bolts and nuts:
1.9.8 | Securing with plain and spring washers | yes/no
1.9.9 | Minimum quality | -
1.9.10 | Tests according to VII-5 Technical Specification | yes/no | yes

## 2. 132 kV AIS
Technical Data Sheets
BIDDER’S / CONTRACTOR’S GUARANTEED DATA |  | Unit | Data required | Data offered
No. | Description
2 | 132 kV Air Insulated Switchgear (AIS)
2.1 | 132 kV Circuit Breaker
2.1.1 | Manufacturer | -
2.1.2 | Place of manufacture | -
2.1.3 | Model designation | -
2.1.4 | Applicable standard | - | IEC 62271-1, IEC 62271-100, IEC 62271-110, IEC 62271-310
2.1.5 | Circuit breaker type | - | Outdoor SF6
2.1.6 | Type of operation |  | three phase / three phase operated
2.1.7 | Operating mechanism: |  | three-phase
2.1.8 | Incomer / coupler bay | - | three-phase
2.1.9 | OHL bay | - | single-phase
2.1.10 | Electrical endurance class |  | E2
2.1.11 | Mechanical endurance class |  | M2
2.1.12 | On line monitoring | yes/no | no
2.1.13 | Point-on-wave controller | yes/no | no
2.1.14 | Number of poles | - | 3
2.1.15 | Nominal voltage | kV | 132
2.1.16 | Rated voltage Ur | kV | 145
2.1.17 | Rated frequency | Hz | 50
2.1.18 | Rated short-duration power frequency withstand voltage: | kVrms | 275
2.1.19 | Rated lightning impulse withstand voltage: | kVpeak | 650
2.1.20 | Rated continuous current | A | 2000
2.1.21 | Rated short-time breaking current | kA | 31.5
2.1.22 | First-pole-to-clear factor | - | 1.3
2.1.23 | Making current peak | kA | 80
2.1.24 | DC time constant of the rated short-circuit breaking current | ms | 60
2.1.25 | Duration of short circuit | s | 3
2.1.26 | Rated break time | ms | ≤40
2.1.27 | Rated closing time | ms | ≤75
2.1.28 | Rated opening time | ms | ≤30
2.1.29 | Number of tripping coils | - | 2
2.1.30 | Number of closing coils | - | 1
2.1.31 | Rated operating sequence (three-phase auto reclosing) | - | O-0.3 s-CO-3 min-CO
2.1.32 | Type of operating mechanism | - | spring operated
2.1.33 | Insulators | - | silicon
2.1.34 | Minimum unified specific creepage distance (USCD) | mm/kV | 43.3
2.1.35 | Temperature operating range | ºC | -25 ‑ +40
2.1.36 | Rated ice thickness | mm | N/A
2.1.37 | Degree of protection of operating mechanism | - | IP55
2.1.38 | Motor rated voltage | V DC | 110
2.1.39 | Operating coils rated voltage | V DC | 110
2.1.40 | Number of auxiliary contacts (NO/NC) | -
2.1.41 | Number of spare auxiliary contacts | % | 15 (as a minimum 3 NO and 3 NC)
2.1.42 | Rated voltage of heater | V AC | 230
2.1.43 | Autoreclosing for the line feeders | - | N/A
2.1.44 | Gas pressure alarm blocking | MPa
2.1.45 | Tests according to VII-5 Technical Specification | yes/no | yes
2.2 | 132kV Disconnector with earthing switch
2.2.1 | Center Break Disconnector with earthing switch
2.2.1.1 | Manufacturer | -
2.2.1.2 | Place of manufacture | -
2.2.1.3 | Model designation | -
2.2.1.4 | Applicable standard | - | IEC 60071, IEC 62271‑1, IEC 62271-102
2.2.1.5 | Type of operation | - | two-columns rotary, three‑phase by common operating mechanism
2.2.1.6 | Type | - | outdoor
2.2.1.7 | Bus transfer capability | A | 1200
2.2.1.8 | Electrical endurance class |  | E0
2.2.1.9 | Mechanical endurance class |  | M2
2.2.1.10 | Number of poles | - | 3
2.2.1.11 | Nominal voltage | kV | 132
2.2.1.12 | Rated voltage Ur | kV | 145
2.2.1.13 | Rated continuous current | A | 2000
2.2.1.14 | Rated frequency | Hz | 50
2.2.1.15 | Rated short-time withstand current | kA | 31.5
2.2.1.16 | Rated duration of short circuit | s | 3
2.2.1.17 | Rated peak withstand current / short circuit making current of earthing switch | kA | 80
2.2.1.18 | Rated short-duration power frequency withstand voltage: | - | -
2.2.1.19 | Phase-to-earth and between the phases | kVrms | 275
2.2.1.20 | Across the open isolating distance | kVrms | 315
2.2.1.21 | Rated lightning impulse withstand voltage: | - | -
2.2.1.22 | Phase-to-earth and between the phases | kVpeak | 650
2.2.1.23 | Across the open isolating distance | kVpeak | 750
2.2.1.24 | Insulators | - | silicon
2.2.1.25 | Minimum Unified Specific Creepage Distance (USCD) | mm/kV | 43.3
2.2.1.26 | Temperature operating range | ºC | -25 ‑ +40
2.2.1.27 | Rated ice thickness | mm | N/A
2.2.1.28 | Type of operating mechanism | - | motor operated / manually in case of emergency
2.2.1.29 | Degree of protection of operating mechanism | - | IP 55
2.2.1.30 | Drive rated voltage | V DC | 110
2.2.1.31 | Heaters rated voltage | V AC | 230
2.2.1.32 | Number of auxiliary contacts (NO/NC) | -
2.2.1.33 | Number of spare auxiliary contacts | % | 15 (as a minimum 3 NO and 3 NC)
2.2.1.34 | Number of earthing switches | - | 1
2.2.1.35 | Earthing switches induced current and voltage class | - | B
2.2.1.36 | Operating mechanism of earthing switches | - | motor operated / manually in case of emergency
2.2.1.37 | Tests according to VII-5 Technical Specification | yes/no | yes
2.2.2 | Pantograph Disconnector with earthing switch
2.2.2.1 | Manufacturer | -
2.2.2.2 | Place of manufacture | -
2.2.2.3 | Model designation | -
2.2.2.4 | Applicable standard | - | IEC 60071, IEC 62271‑1, IEC 62271-102
2.2.2.5 | Type of operation | - | pantograph, single phase / three‑phase by common operating mechanism
2.2.2.6 | Type | - | outdoor
2.2.2.7 | Bus transfer capability | A | 1200
2.2.2.8 | Electrical endurance class |  | E0
2.2.2.9 | Mechanical endurance class |  | M2
2.2.2.10 | Number of poles | - | 3
2.2.2.11 | Nominal voltage | kV | 132
2.2.2.12 | Rated voltage Ur | kV | 145
2.2.2.13 | Rated continuous current | A | 2000
2.2.2.14 | Rated frequency | Hz | 50
2.2.2.15 | Rated short-time withstand current | kA | 31.5
2.2.2.16 | Rated duration of short circuit | s | 3
2.2.2.17 | Rated peak withstand current / short circuit making current of earthing switch | kA | 80
2.2.2.18 | Rated short-duration power frequency withstand voltage: | - | -
2.2.2.19 | Phase-to-earth and between the phases | kVrms | 275
2.2.2.20 | Across the open isolating distance | kVrms | 315
2.2.2.21 | Rated lightning impulse withstand voltage: | - | -
2.2.2.22 | Phase-to-earth and between the phases | kVpeak | 650
2.2.2.23 | Across the open isolating distance | kVpeak | 750
2.2.2.24 | Insulators | - | silicon
2.2.2.25 | Minimum Unified Specific Creepage Distance (USCD) | mm/kV | 43.3
2.2.2.26 | Temperature operating range | ºC | -25 ‑ +40
2.2.2.27 | Rated ice thickness | mm | N/A
2.2.2.28 | Type of operating mechanism | - | motor operated / manually in case of emergency
2.2.2.29 | Degree of protection of operating mechanism | - | IP55
2.2.2.30 | Drive rated voltage | V DC | 110
2.2.2.31 | Heaters rated voltage | V AC | 230
2.2.2.32 | Number of auxiliary contacts (NO/NC) | -
2.2.2.33 | Number of spare auxiliary contacts | % | 15 (as a minimum 3 NO and 3 NC)
2.2.2.34 | Number of earthing switches | - | 1
2.2.2.35 | Earthing switches induced current and voltage class | - | B
2.2.2.36 | Operating mechanism of earthing switches | - | motor operated / manually in case of emergency
2.2.2.37 | Tests according to VII-5 Technical Specification | yes/no | yes
2.3 | 132 kV Current Transformer
2.3.1 | Manufacturer | -
2.3.2 | Model designation
2.3.3 | Place of manufacture | -
2.3.4 | Applicable standard | - | IEC 61869-1
IEC 61869-2
| Type | - | Outdoor
| Nominal voltage | kV | 132
| Rated voltage | kV | 145
| Rated short-time current | kA | 31.5
| Duration of short circuit | s | 3
2.3.5 | Rated peak withstand current | kApeak | 80
2.3.6 | Type of insulators | - | silicon
2.3.7 | Rated extended primary current in percentage of rated primary current | % | 120
Rated primary current
2.3.8 | · for measuring/metering/prot. | A | 1250-1500-2000
| · for busbar protection | A | 2000
2.3.9 | Number of cores:
2.3.10 | · for measuring | - | 1
2.3.11 | · for metering | - | 1
2.3.12 | · for protection | - | 3
2.3.13 | Rated secondary current:
2.3.14 | · for measuring | A | 1
2.3.15 | · for metering | A | 1
2.3.16 | · for protection | A | 1
2.3.17 | Accuracy class:
2.3.18 | · for measuring | - | 0.5 M
2.3.19 | · for metering |  | 0.2S
2.3.20 | · for protection | - | 5P 20
2.3.21 | Rated burden:
2.3.22 | · for measuring core | VA | 15
2.3.23 | · for metering core | VA | 15
2.3.24 | · for protection cores | VA | 30
2.3.25 | Minimum Unified Specific Creepage Distance (USCD) | mm/kV | 43.3
2.3.26 | Rated lightning impulse withstand voltage | kVpeak | 650
2.3.27 | Rated short-duration power frequency withstand voltage | kVrms | 275
2.3.28 | Tests according to VII-5 Technical Specification | yes/no | yes
2.4 | 132 kV Capacitive Voltage Transformer
2.4.1 | Manufacturer | - | -
2.4.2 | Place of manufacture | - | -
2.4.3 | Model designation | - | -
2.4.4 | Applicable standard | - | IEC 60071-1
IEC 60071-2
IEC 61869-1
IEC 61869-5
IEC 60358-1
IEC 60529
IEC 60815
2.4.5 | Type | - | outdoor, capacitor type
2.4.6 | Highest voltage for equipment Um | kV | 145
2.4.7 | Rated primary voltage | kV | 132 / √3
2.4.8 | Number of secondary windings |  | 3
2.4.9 | · for protection | - | combined
2.4.10 | · for measurement | - | combined
2.4.11 | · for metering | - | 1
2.4.12 | Rated secondary voltage:
2.4.13 | · protection winding | V | 110 / √3
2.4.14 | · measurement winding | V | 110 / √3
2.4.15 | · metering winding | V | 110 / √3
2.4.16 | Accuracy class for protection | - | 3P
2.4.17 | Accuracy class for measurement | - | 0.5
2.4.18 | Accuracy class for metering | - | 0.2S
2.4.19 | Total rated burden secondary windings | VA | 3 x 50
2.4.20 | Type of insulators | - | silicon
2.4.21 | Minimum Unified Specific Creepage Distance (USCD) | mm/kV | 43.3
2.4.22 | Rated lightning impulse withstand voltage | kVpeak | 650
2.4.23 | Rated power frequency withstand voltage | kVrms | 275
2.4.24 | Tests according to VII-5 Technical Specification | yes/no | yes
2.5 | 132kV Lightning Arrester and Discharge Counter
2.5.1 | Manufacturer | - | -
2.5.2 | Place of manufacture | - | -
2.5.3 | Model designation | - | -
2.5.4 | Applicable standard | - | IEC 60071-1
IEC 60071-2
IEC 60099-4
IEC 60099-5
IEC 60529
IEC 60815
2.5.5 | Type | - | Outdoor, silicon-housed
2.5.6 | System data:
2.5.7 | · Nominal system voltage | kV | 132
2.5.8 | · Highest system voltage | kV | 145
2.5.9 | · System frequency | Hz | 50
2.5.10 | Rated voltage Ur | kV | 108
2.5.11 | Maximum continuous operating voltage Uc | kV | 86
2.5.12 | Minimum Unified Specific Creepage Distance (USCD) | mm/kV | 43.3
2.5.13 | Rated discharge current | kA | 10 / 20 subject to calculation
2.5.14 | Thermal energy rating | kJ/kV | 10
2.5.15 | Separate earthing rod per SA, 150 mm2 | yes/no | yes
2.5.16 | Discharge Counter:
2.5.17 | Manufacturer | -
2.5.18 | Model designation | -
2.5.19 | Display | -
2.5.20 | Number of impulses | yes/no | yes
2.5.21 | Leakage current measurement, total current | yes/no | yes
2.5.22 | Protection class | - | IP 55 W
2.5.23 | Number of counters per three (3) 1-ph arresters | - | 3
2.5.24 | Tests according to VII-5 Technical Specification | yes/no | yes
2.6 | 132 kV Post Insulator
2.6.1 | Manufacturer | -
2.6.2 | Place of manufacture | -
2.6.3 | Type | - | outdoor, porcelain/silicon
2.6.4 | Applicable standard | - | IEC 60071-1
IEC 60071-2
IEC 60168
IEC 60273
IEC 60815
IEC 61952
IEC 62217
IEC 62231-1
IEC 61462
IEC 62772
2.6.5 | Model designation | -
2.6.6 | Number of stacks | - | single
2.6.7 | IEC post insulator designation | -
2.6.8 | System nominal voltage | kV | 132
2.6.9 | Highest voltage of equipment | kV | 145
2.6.10 | Rated lightning impulse withstand voltage, dry | kVpeak | 650
2.6.11 | Rated switching impulse withstand voltage, wet | kVpeak | 275
2.6.12 | Minimum Unified Specific Creepage Distance (USCD) | mm/kV | 43.3
2.6.13 | Minimum failing load, bending | kN
2.6.14 | Tests according to VII-5 Technical Specification | yes/no | yes
2.7 | 132 kV Insulator String
2.7.1 | Insulator units
2.7.2 | Applicable standard | - | IEC 60071-1
IEC 60071-2
IEC 60120
IEC 60383-1
IEC 60383-2
IEC 60305
IEC 60372
IEC 60815
IEC 61109
IEC 61466
2.7.3 | Manufacturer | -
2.7.4 | Type | -
2.7.5 | Insulating body material | - | silicon
2.7.6 | Rated electromechanical or mechanical strength | kN
2.7.7 | Max. shed diameter | mm
2.7.8 | Minimum Unified Specific Creepage Distance (USCD) | mm/kV | 43.3
2.7.9 | Tests according to VII-5 Technical Specification | yes/no | yes
2.8 | 132 kV Tubular Busbar
2.8.1 | Applicable standard | - | DIN 43670
DIN 46276-1
EN 755-1
EN 755-2
EN 755-7
2.8.2 | Manufacturer | -
2.8.3 | Place of manufacture | -
2.8.4 | Type | -
2.8.6 | Rated current | A
2.8.7 | Rated short time current (3s) | kA
2.8.9 | Tubular type: | - | Al 3inch SC80
2.8.11 | Internal diameter | mm | -
2.8.12 | Tube weight | kg/m | -
2.8.13 | Theoretical breaking force | kN | -
2.8.14 | Ohmic resistance at 20°C | Ω/km | -
2.8.15 | Tests according to VII-5 Technical Specification | yes/no | yes

## 3. 220 kV GIS
Technical Data Sheets
BIDDER’S / CONTRACTOR’S GUARANTEED DATA |  | Unit | Data required | Data offered
No. | Description
3 | 220 kV Gas Insulated Switchgear (GIS)
3.1 | General
3.1.1 | Manufacturer | -
3.1.2 | Place of manufacture | -
3.1.3 | Model designation | -
3.1.4 | Type | - | Metal enclosed, gas insulated GIS- indoor
3.1.5 | Applicable standard | - | IEC 62271-203, 62271-1, 60270, 60376, 60480
3.1.6 | Nominal voltage of system | kVrms | 220
3.1.7 | Rated voltage of system | kVrms | 245
3.1.8 | Rated frequency | Hz | 50
3.1.9 | Rated short-duration power frequency withstand voltage:
3.1.10 | - Common Value | kVrms | 460
3.1.11 | - Across the isolating distance | kVrms | 530
3.1.12 | Rated lightning impulse withstand voltage:
3.1.13 | - Common Value | kVpeak | 1050
3.1.14 | - Across the isolating distance | kVpeak | 1200
3.1.15 | Rated short-time withstand current (3s) | kA | 40
3.1.16 | Rated peak withstand current | kA | 100
3.1.17 | Rated current (busbar)
3.1.18 | Lekhnath | A | 3150
3.1.19 | Damauli | A | 4000
3.1.20 | Rated current (feeders)
3.1.21 | Lekhnath | A | 2500
3.1.22 | Damauli | A | 3150
3.1.23 | Rated current (bus coupler / bus section)
3.1.24 | Lekhnath | A | 3150
3.1.25 | Damauli | A | 4000
3.1.26 | Type of busbars | - | Double
3.1.27 | Type of enclosure (bus bar/feeder) | - | 1-phase / 1-phase
3.1.28 | Material of enclosure for:
3.1.29 | - Circuit breaker | - | Al
3.1.30 | - Busbars | - | Al
3.1.31 | - Other compartments | - | Al
3.1.32 | Applicable standard for SF6 pressurized enclosures | - | EN 50052, 50064, 50068, 50069, 50089
3.1.33 | Minimum safety factor for switchgear (GIS housings/steel supports) | - | ≥ 2,5
3.1.34 | Seismic factor according to IEEE 693 figure A.1 | g | 0,5
3.1.35 | Suitability for the site climate/temperature range:
3.1.36 | Lekhnath | °C | 0 - 40
3.1.37 | Damauli | °C | 0 - 40
3.1.38 | Material and cross-section of bus bar conductor | .../ mm2
3.1.39 | Material and cross-section of feeder bus-duct conductor | .../ mm2
3.1.40 | Material of contacts (indicate bi-metallic where used) | - | Cu/Ag
3.1.41 | Type of contact | - | Tulip/plug-in
3.1.42 | Surface treatment of GIS housings:
3.1.43 | - Indoor paint / layer thickness | RAL / µm
3.1.44 | - Outdoor paint / layer thickness | RAL / µm
3.1.45 | - Flange treatment (outdoor) | - | Add number of technical description
3.1.46 | Colour of partition insulators | RAL
3.1.47 | Colour of local control cubicle | RAL
3.1.48 | Minimum subdivision of GIS switchgear (partition):
3.1.49 | - Busbars per each feeder | - | Yes
3.1.50 | - Busbar isolator | - | Yes
3.1.51 | - Circuit breaker | - | Yes
3.1.52 | - Feeder disconnector and cable end unit | - | Yes
3.1.53 | - Voltage transformer | - | Yes
3.1.54 | - Current transformer | - | Yes
3.1.55 | - Surge arrster (if any) | - | Yes
3.1.56 | - Max. lenght/volume of gas insulated bus duct | Meter/Litre | …/…
3.1.57 | Maximum size of gas compartment | Litre
3.1.58 | Maximum evaquation time of gas compartment | hrs | < 2
3.1.59 | Method of compensation of expansion and contraction:
3.1.60 | - For busbar conductors | - | Expansion
3.1.61 | - For busbar enclosures | - | Expansion
3.1.62 | Type/ material of pressure relief device | - | Rupture disc / …
3.1.63 | Rupturing pressure of pressure relief device (circuit breaker/others) | MPa | …/…
3.1.64 | Type of filter employed for moisture absorption | - | Molecular Sieve
3.1.65 | Design lifetime of moisture absorbent | Years | > 10
3.1.66 | Total mass of switchgear / haviest transportation unit | kg | …/…
3.1.67 | Size of maximum transportation unit (L x W x H) | m
3.1.68 | Mass of heaviest single component to be handled during erection | kg
3.1.69 | Mass of heaviest single indoor component to be handled during erection with the indoor crane | kg
3.1.70 | Bay width (centre to centre) | m
3.1.71 | Indoor footprint of initial GIS | m x m
3.1.72 | Indoor footprint including extension | m x m
3.1.73 | Minimum indoor crane hook height | m
3.1.74 | Indoor crane lifting force | t | ≥ 6
3.1.75 | Crane with 2 speeds suitable for GIS installation | - | Yes
3.1.76 | Applicable standard for new SF6 gas | - | IEC 60376
3.1.77 | Density of gas in:
3.1.78 | - Circuit breaker compartment | g/l
3.1.79 | - Other than circuit breaker compartment | g/l
3.1.80 | Rated filling pressure at 20ºC (CB/others) | MPa
3.1.81 | 1st alarm pressure at 20ºC (CB/others) | MPa
3.1.82 | Circuit breaker blocking pressure at 20ºC (Close/Open) | MPa
3.1.83 | Maximum SF6 leakage rate | % / year | < 0,1
3.1.84 | Design pressure of enclosures (circuit breaker/ others) | MPa | …/…
3.1.85 | Type test presure of enclosures (circuit breaker/others | MPa | …/…
3.1.86 | Routine test pressure of casted enclosures (circuit breaker/others) | MPa | …/…
3.1.87 | Routine test pressure of welded enclosures (circuit breaker/others) | MPa
3.1.88 | Design pressure of gas tight barrier insulator | MPA
3.1.89 | Routine test pressure of gas tight barrier insulator | MPa
3.1.90 | Withstand voltage at SF6 gas atmospheric pressure | kV | 245
3.1.91 | Minimum gas service period | years | > 10
3.1.92 | Document number showing maximum allowable dewpoint depending on temperature for different gas filling/compartments | - | to be provided with Tender
3.1.93 | Recommended inspection/maintenance intervals | years
3.1.94 | Neutral earthing | - | solidly
3.1.95 | Document number showing the Inspection and Test Plan for the complete GIS scope of supply including FAT | - | to be provided with Tender
3.2 | Circuit breaker
3.2.1 | Manufacturer | -
3.2.2 | Place of manufacture | -
3.2.3 | Model designation | -
3.2.4 | Type | - | Self-blast pressure buffer,SF6
3.2.5 | Applicable standard | - | IEC 62271-1 lEC 62271-203, IEC 62271-100
3.2.6 | Type of quenching medium |  | SF6
3.2.7 | Interrupter units per pole | pcs | 1
3.2.8 | Rated voltage | kV | 245
3.2.9 | Rated short-duration power frequency withstand voltage:
3.2.10 | - Common Value | kVrms | 460
3.2.11 | - Across the isolating distance | kVrms | 530
3.2.12 | Rated lightning impulse withstand voltage:
3.2.13 | - Common Value | kVpeak | 1050
3.2.14 | - Across the isolating distance | kVpeak | 1200
3.2.15 | Rated frequency | Hz | 50
3.2.16 | Number of phases | - | 3
3.2.17 | Rated current (bus coupler/feeders)
3.2.18 | Lekhnath | A | 3150/2500
3.2.19 | Damauli | A | 4000/3150
3.2.20 | Rated short-time withstand current (3s) | kA | 40
3.2.21 | Rated peak withstand current | kA | 100
3.2.22 | Rated making current | kA | 100
3.2.23 | Rated cable charging breaking current | A
3.2.24 | Maximum capacitive breaking current: | A | to IEC 62271-100
3.2.25 | - Rated line charging breaking current | A | 125
3.2.26 | - Rated cable charging breaking current | A | 250
3.2.27 | - Rated Single/Back to Back Capacitor bank breaking current | A | 400
3.2.28 | - Rated single capacitor bank breaking current | A | 400
3.2.29 | Rated breaking current asymmetrical | kA
3.2.30 | - %dc | %dc
3.2.31 | Rated breaking current under out-of-phase conditions | kA
3.2.32 | Terminal fault | kpp / p.u. | 1,3
3.2.33 | Short-Line-fault | kpp / p.u. | 1
3.2.34 | Out-of-phase | kpp / p.u. | 2
3.2.35 | Rated small inductive/reactor breaking currents of: |  | to IEC 62271-100
3.2.36 | - Small inductive loads | A
3.2.37 | - Reactor | A
3.2.38 | Maximum overvoltage factor when interrupting rated line/cable/ capacitor bank charging currents | pu | 2,5 (or restrike free)
3.2.39 | Maximum overvoltage factor when switching small inductive/reactor currents | pu | 2,5
3.2.40 | Number of tripping coils | - | 2
3.2.41 | Number of closing coils | - | 1
3.2.42 | Type of operation | - | single and three phase
3.2.43 | Rated operating sequence | - | 0 - 0,3 s - CO - 3 min - CO
3.2.44 | Opening time | ms | < 30
3.2.45 | Breaking time | ms | < 50
3.2.46 | Closing time | ms | < 60
3.2.47 | Dead time | ms | 300
3.2.48 | Maximum time interval between opening of first and last phase of three phase circuit breakers | ms | ≤ 3
3.2.49 | Closing time from energization of close coil to latching of circuit breaker in fully closed position | ms
3.2.50 | Making time (energization of close coil to contact touch):
3.2.51 | - Without current | ms
3.2.52 | - 100% making current | ms
3.2.53 | Minimum time from extinction of main arc to contact make during auto-reclosing duty | ms | 300
3.2.54 | Mechanical life of circuit breaker | - | M2
3.2.55 | Electrical contact life in number of operations at:
3.2.56 | - Rated current- 4000/4000A | - | 10 000
3.2.57 | - Fault current - 40 kA | - | 15
3.2.58 | - Cumulative ampere rating | -
3.2.59 | Number of current interrupting break units in series per phase | - | One
3.2.60 | Type of operating mechanism | - | Spring-charged
3.2.61 | Type of power device (motor-charged)
3.2.62 | - For closing | - | Spring-charged
3.2.63 | - For opening | - | Spring-charged
3.2.64 | Motor power | W
3.2.65 | Hand operating facility | - | Yes
3.2.66 | Hand charging facility | - | Yes
3.2.67 | Manual spring release | - | Yes
3.2.68 | Mechanical on/off indicator | - | Yes
3.2.69 | Mechanical spring charge/discharge indication | - | Yes
3.2.70 | Charging time | s
3.2.71 | Number of tripping coils | - | 2
3.2.72 | Number of closing coils | - | 1
3.2.73 | Rated power of close coil | W
3.2.74 | Rated power of trip coil | W
3.2.75 | Number of auxiliary contacts (NO/NC) | -
3.2.76 | Mechanical endurance | - | M2
3.2.77 | Capasitive current switching | - | C2
3.2.78 | Nominal control and operating voltage | V DC | 220
3.2.79 | Nominal heater voltage | V AC | 230
3.2.80 | Total load of heaters for circuit breaker | W
3.2.81 | Total SF6 gas weight of circuit breaker | kg
3.2.82 | Total weight of the circuit breaker (three phases) | kg
3.2.83 | Emergency Trip Facility during failure of DC supply | - | Yes
3.2.84 | Protection class of drive mechanism box | - | IP 55
3.3 | Disconnectors
3.3.1 | Manufacturer | -
3.3.2 | Place of manufacturing | -
3.3.3 | Model designation | -
3.3.4 | Type | - | single equipment /not combined
3.3.5 | Applicable standard | - | IEC 62271-1 IEC 62271-102 62271-203
3.3.6 | Type of operating mechanism | - | Motor & Manual
3.3.7 | Rated voltage | kV | 245
3.3.8 | Rated current bus bar, bus coupler
3.3.9 | Lekhnath | A | 3150
3.3.10 | Damauli | A | 4000
3.3.11 | Rated current feeders
3.3.12 | Lekhnath | A | 2500
3.3.13 | Damauli | A | 3150
3.3.14 | Rated lightning impulse withstand voltage
3.3.15 | - Common Value | kVpeak | 1050
3.3.16 | - Across the isolating distance | kVpeak | 1200
3.3.17 | Rated power frequency withstand voltage
3.3.18 | - Common Value | kVrms | 460
3.3.19 | - Across the isolating distance | kVrms | 530
3.3.20 | Rated frequency | Hz | 50
3.3.21 | Rated short time withstand current (3s) | kA | 40
3.3.22 | Rated short-circuit peak withstand current | kA | 100
3.3.23 | Maximum capacitive current that can be interrupted by the isolator | A
3.3.24 | Total time from initiation of opening operation to isolator in fully open position | s
3.3.25 | Time from contact separation to extinct of capacitive arc | s
3.3.26 | Total time from initiation of opening operation to time when isolator gap can withstand phase voltage | s
3.3.27 | Bus-transfer current switching ability:
3.3.28 | - bus-transfer current | A | 1600
3.3.29 | - bus transfer voltage | V | 20
3.3.30 | Hand operating facility | - | Yes
3.3.31 | Locking arrangement in on/off position | - | Yes
3.3.32 | Number of auxiliary contacts (NO/NC/others) | -
3.3.33 | Nominal control and operating voltage | V DC | 220
3.3.34 | Automatic isolation of control supplies when DS locked in open position | - | Yes
3.3.35 | Accessibility to operating mechanism from ground level or catwalk | - | Yes
3.3.36 | Nominal heater voltage | V AC | 230
3.3.37 | Total load of heaters for isolator | W
3.3.38 | Rated motor power | W
3.3.39 | Total mass of three phase disconnector complete | kg
3.3.40 | Contact type | - | Tulip/plug-in
3.3.41 | Mechanical endurance | - | M2
3.3.42 | Viewing windows |  | Yes
3.3.43 | Protection class of drive mechanism box | - | IP 55
3.4 | Maintenance earthing switch
3.4.1 | Manufacturer | -
3.4.2 | Place of manufacturing | -
3.4.3 | Model designation | -
3.4.4 | Type | - | single equipment /not combined
3.4.5 | Type of operating mechanism | - | Motor & Manual
3.4.6 | Applicable standard | - | IEC 62271-1 IEC 62271-102 62271-203
3.4.7 | Rated voltage | kV | 245
3.4.8 | Rated lightning impulse withstand voltage phase to earth | kVpeak | 1050
3.4.9 | Rated power frequency withstand voltage phase to earth | kVrms | 460
3.4.10 | Rated frequency | Hz | 50
3.4.11 | Rated short time withstand current (3s) | kA | 40
3.4.12 | Rated short-circuit peak withstand current | kA | 100
3.4.13 | Total opening time | s
3.4.14 | Total closing time | s
3.4.15 | Hand operating facility | - | Yes
3.4.16 | Locking arrangement in on/off position | - | Yes
3.4.17 | Number of auxiliary contacts (NO/NC) | -
3.4.18 | Nominal control and operating voltage | V DC | 220
3.4.19 | Automatic isolation of control supplies when DS locked in open position | - | Yes
3.4.20 | Accessibility to operating mechanism from ground level or catwalk | - | Yes
3.4.21 | Nominal heater voltage | V AC | 230
3.4.22 | Total load of heaters for isolator | W
3.4.23 | Rated motor power | W
3.4.24 | Rated power of operation coil | W
3.4.25 | Rated insulation of brought out connection | kV | 10
3.4.26 | Total mass of maintenance earthing switch | kg
3.4.27 | Contact type |  | Tulip/plug-in
3.4.28 | Viewing windows |  | Yes
3.4.29 | Protection class of drive mechanism box | - | IP 55
3.5 | High speed earthing switch
3.5.1 | Manufacturer | -
3.5.2 | Place of manufacturing | -
3.5.3 | Model designation | -
3.5.4 | Type | - | attached unit
3.5.5 | Type of operating mechanism | - | Motor & Manual spring charged
3.5.6 | Applicable standard | - | IEC 62271-1 IEC 62271-102 62271-203
3.5.7 | Rated voltage | kV | 245
3.5.8 | Rated lightning impulse withstand voltage phase to earth | kVpeak | 1050
3.5.9 | Rated power frequency withstand voltage phase to earth | kVrms | 460
3.5.10 | Rated frequency | Hz | 50
3.5.11 | Rated short time withstand current (3s) | kA | 40
3.5.12 | Rated short-circuit peak withstand current | kA | 100
3.5.13 | Mechanical endurance / Number of making operations at rated making current (40kA) |  | E1
3.5.14 | Rated capacitive symmetrical making current | A
3.5.15 | Rated inductive symmetrical making current | A
3.5.16 | Total time from initiation of opening operation to earth switch in fully open position | s
3.5.17 | Making time | ms
3.5.18 | Charging time | s
3.5.19 | Hand operating facility | - | Yes
3.5.20 | Locking arrangement in on/off position | - | Yes
3.5.21 | Number of auxiliary contacts (NO/NC) | -
3.5.22 | Nominal control and operating voltage | V DC | 220
3.5.23 | Automatic isolation of control supplies when HES locked in open position | - | Yes
3.5.24 | Accessibility to operating mechanism from ground level or catwalk | - | Yes
3.5.25 | Nominal heater voltage | V AC | 230
3.5.26 | Total load of heaters for isolator | W
3.5.27 | Rated motor power | W
3.5.28 | Rated power of operation coil | W
3.5.29 | Rated insulation of brought out connection | kV | 10
3.5.30 | Total mass of high speed earthing switch | kg
3.5.31 | Contact type |  | Tulip/plug-in
3.5.32 | Viewing windows |  | Yes
3.5.33 | Protection class of drive mechanism box | - | IP 55
3.6 | Current transformer |  | integrated
3.6.1 | Manufacturer | -
3.6.2 | Place of manufacturing | -
3.6.3 | Type | -
3.6.4 | Applicable standard | - | IEC 61869-1 IEC 61869-2 IEC 62271-1 IEC 62271-203
3.6.5 | Rated voltage | kV | 245
3.6.6 | Rated power frequency withstand voltage phase to earth (GIS) |  | 460
3.6.7 | Rated lightning impulse withstand voltage Phase to earth (GIS) |  | 1050
3.6.8 | Rated power frequency voltage of secondary winding | kV | 3
3.6.9 | Inter-turn test | kVpeak | 4,5
3.6.10 | Rated frequency | Hz | 50
3.6.11 | Rated short-time withstand current (3 s) | kA | 40
3.6.12 | Rated short-circuit peak withstand current | kA | 100
3.6.13 | Rated extended primary current in percentage of rated primary current | % | 120
3.6.14 | Lekhnath & Damauli Overhead line bay current transformer
3.6.14.1 | - number of cores | -
3.6.14.2 | Metering |  | 1
3.6.14.3 | Measuring |  | 1
3.6.14.4 | Protetction |  | 2
3.6.14.5 | Busbar Protection |  | 1
3.6.14.6 | - Ratio
3.6.14.7 | Metering / measuring / protection | A | 1000-1500-2000/1
3.6.14.8 | Busbar Protection Leknath Damauli | A | 3000/1 4000/1
3.6.14.9 | - Class
3.6.14.10 | Metering | - | 0.2S
3.6.14.11 | Measuring | - | 0,5 FS 5
3.6.14.12 | Protetction | - | 5P20
3.6.14.13 | Busbar Protection | - | 5P20
3.6.14.14 | - Rated output (burden to be 25-100 % rated burden)
3.6.14.15 | Metering | VA | 15
3.6.14.16 | Measuring | VA | 15
3.6.14.17 | Protetction | VA | 30
3.6.14.18 | Busbar Protection | VA | 30
3.6.15 | Lekhnath Bus coupler bay current transformer (both sides)
3.6.15.1 | - number of cores | -
3.6.15.2 | Metering |  | -
3.6.15.3 | Measuring |  | 1
3.6.15.4 | Protetction |  | 1
3.6.15.5 | Busbar Protection |  | 1
3.6.15.6 | - Ratio
3.6.15.7 | Metering / measuring / protection | A | 2000-2500-3000/1
3.6.15.8 | Busbar Protection | A | 3000/1
3.6.15.9 | - Class
3.6.15.10 | Metering | - | -
3.6.15.11 | Measuring | - | 0,5 FS 5
3.6.15.12 | Protetction | - | 5P20
3.6.15.13 | Busbar Protection | - | 5P20
3.6.15.14 | - Rated output (burden to be 25-100 % rated burden)
3.6.15.15 | Metering | VA | -
3.6.15.16 | Measuring | VA | 15
3.6.15.17 | Protetction | VA | 30
3.6.15.18 | Busbar Protection | VA | 30
3.6.16 | Damauli Bus coupler bay / Bus Sectionaliser bay current transformer (both sides
3.6.16.1 | - number of cores | -
3.6.16.2 | Metering |  | -
3.6.16.3 | Measuring |  | 1
3.6.16.4 | Protetction |  | 1
3.6.16.5 | Busbar Protection |  | 1
3.6.16.6 | - Ratio
3.6.16.7 | Metering / measuring / protection | A | 1500-2500-4000/1
3.6.16.8 | Busbar Protection | A | 4000/1
3.6.16.9 | - Class
3.6.16.10 | Metering | - | -
3.6.16.11 | Measuring | - | 0,5 FS 5
3.6.16.12 | Protetction | - | 5P20
3.6.16.13 | Busbar Protection | - | 5P20
3.6.16.14 | - Rated output (burden to be 25-100 % rated burden)
3.6.16.15 | Metering | VA | -
3.6.16.16 | Measuring | VA | 15
3.6.16.17 | Protetction | VA | 30
3.6.16.18 | Busbar Protection | VA | 30
3.6.17 | Lekhnath 220/132/33kV Auto-transformer bay current transformer
3.6.17.1 | - number of cores | -
3.6.17.2 | Metering |  | 1
3.6.17.3 | Measuring |  | 1
3.6.17.4 | Protetction |  | 2
3.6.17.5 | Busbar Protection |  | 1
3.6.17.6 | - Ratio
3.6.17.7 | Metering / measuring / protection | A | 500-750-1250/1
3.6.17.8 | Busbar Protection | A | 3000/1
3.6.17.9 | - Class
3.6.17.10 | Metering | - | 0.2S
3.6.17.11 | Measuring | - | 0,5 FS 5
3.6.17.12 | Protetction | - | 5P20
3.6.17.13 | Busbar Protection | - | 5P20
3.6.17.14 | - Rated output (burden to be 25-100 % rated burden)
3.6.17.15 | Metering | VA | 15
3.6.17.16 | Measuring | VA | 15
3.6.17.17 | Protetction | VA | 30
3.6.17.18 | Busbar Protection | VA | 30
3.6.18 | Damauli 220/132 kV Power-transformer bay current transformer
3.6.18.1 | - number of cores | -
3.6.18.2 | Metering |  | 1
3.6.18.3 | Measuring |  | 1
3.6.18.4 | Protetction |  | 2
3.6.18.5 | Busbar Protection |  | 1
3.6.18.6 | - Ratio
3.6.18.7 | Metering / measuring / protection | A | 200-400-600/1
3.6.18.8 | Busbar Protection | A | 4000
3.6.18.9 | - Class
3.6.18.10 | Metering | - | 0.2S
3.6.18.11 | Measuring | - | 0,5 FS 5
3.6.18.12 | Protetction | - | 5P20
3.6.18.13 | Busbar Protection | - | 5P20
3.6.18.14 | - Rated output (burden to be 25-100 % rated burden)
3.6.18.15 | Metering | VA | 15
3.6.18.16 | Measuring | VA | 15
3.6.18.17 | Protetction | VA | 30
3.6.18.18 | Busbar Protection | VA | 30
3.7 | Inductive voltage transformer (bus bars)
3.7.1 | Manufacturer
3.7.2 | Place of manufacturing
3.7.3 | Type |  | Inductive, SF6 gas insulated
3.7.4 | Applicable standard |  | IEC 62271-1 IEC 62271-203 IEC 61869-1 IEC 61869-3
3.7.5 | Separated from the bus bar with disconnector |  | Yes
3.7.6 | Rated primary voltage | kV | 245
3.7.7 | Rated frequency | HZ | 50
3.7.8 | Rated lightning impulse phase to earth | kVpeak | 1050
3.7.9 | Rated power frequency withstand voltage phase to earth | kVrms | 460
3.7.10 | Maximum permissible partial discharge level Um | pC | 10
3.7.11 | Maximum permissible partial discharge level 1.2Um/√3 | pC | 5
3.7.12 | Method of suppressing Ferro-resonance phenomena | -
3.7.13 | Bus bar voltage transformer
3.7.14 | - Number of secondary | - | 2
3.7.15 | - Rated transformation ratio | kV | 220/√3 /0.11/√3/0.11/√3
3.7.16 | - Rated accuracy class
3.7.17 | Secondary winding 1 | - | 0,2 / 3P
3.7.18 | Secondary winding 2 | - | 0,2 / 3P
3.7.19 | - Rated output
3.7.20 | Secondary winding 1 | VA | 100
3.7.21 | Secondary winding 2 | VA | 100
3.7.22 | - Mass of voltage transformer | kg
3.7.23 | - Quantity of SF6 gas at rated filling pressure | kg
3.7.24 | Rated voltage factor
3.7.25 | - continuous |  | 1,2
3.7.26 | - 30 s |  | 1,5
3.8 | Bus ducts
3.8.1 | Manufacturer
3.8.2 | Place of manufacturing
3.8.3 | Type
3.8.4 | Applicable standard |  | IEC 62271-1 IEC 62271-203
3.8.5 | Common enclosed phases | pcs | single phase
3.8.6 | Rated current at max. ambient temperature and sun radiation
3.8.7 | Lekhnath |  | 2000 A at 40 ⁰C
3.8.8 | Damauli |  | 3150 A at 40 ⁰C
3.8.9 | Inductance | H/m
3.8.10 | Capacitance | pF/m
3.8.11 | Resistance of enclosure | Ohm/m
3.8.12 | Resistance of conductor | Ohm/m
3.8.13 | Surge impedance | Ohm
3.8.14 | Quantity of SF6 gas at rated filling pressure (single phase):
3.8.15 | - shortest bus duct | kg
3.8.16 | - maximum gas compartment | kg
3.8.17 | - longest complete feeder bus duct | kg
3.9 | GIS SF6 air bushing
3.9.1 | Manufacturer | -
3.9.2 | Place of manufacturing | -
3.9.3 | Type | -
3.9.4 | Model designation | -
3.9.5 | Applicable standard | - | IEC 62271-1 IEC 62271-203 IEC 60137 IEC 61643
3.9.6 | Type of internal insulation |  | Gas-insulated
3.9.7 | Type of external insulation |  | Composite
3.9.8 | Shed profile | - | alternating
3.9.9 | Highest voltage for equipment Um | kV | 245
3.9.10 | Rated phase-to-earth voltage |  | 0,8 x Um
3.9.11 | Rated lightning impulse withstand voltage | kVpeak | 1050
3.9.12 | Power-frequency withstand voltage | kVrms | 460
3.9.13 | Rated current at max. ambient temperature and sun radiation
3.9.14 | Lekhnath |  | 2000 A at 40 ⁰C
3.9.15 | Damauli |  | 3150 A at 40 ⁰C
3.9.16 | Rated short time current (3s) | kA | 40
3.9.17 | Rated dynamic current | kA | 100
3.9.18 | Inner filling of the bushing |  | SF6
3.9.19 | Rated design pressure | MPa
3.9.20 | SF6 filling; pressure at 20⁰C | Mpa
3.9.21 | Min. SF6 service pressure | MPa
3.9.22 | Routine test pressure | MPa
3.9.23 | Bursting pressure | MPa
3.9.24 | Max. leakage rate at filling pressure | % | ≤ 0,1
3.9.25 | Minimum Unified Specific Creepage Distance (USCD) | mm/kV | 43,3
3.9.26 | Current conductor material | -
3.9.27 | Current conductor diameter | mm
3.9.28 | Cantilever test load | N
3.9.29 | Cantilever opertion load | N
3.9.30 | Type of line termination | -
3.9.31 | Seismic acceleration according to IEEE 693 figure A.1 | g | 0.5
3.9.32 | Seismic qualification according IEC 61643 | - | Yes
3.9.33 | Quantity of SF6 gas (if any) at rated filling pressure | kg
3.9.34 | Weight | kg
3.10 | GIS lightning arrester - gapless zinc-oxide type (if any)
3.10.1 | Manufacturer | -
3.10.2 | Place of manufacturing
3.10.3 | Type | - | MO
3.10.4 | Applicable standard |  | IEC 60099-4 IEC 60099-5 IEC 62271-1 IEC 62271-203
3.10.5 | Nominal voltage | kVrms | 220
3.10.6 | Rated voltage | kVrms | 245
3.10.7 | Rated frequency | Hz | 50
3.10.8 | Rated lightning impulse withstand voltage phase to earth | kVpeak | 1050
3.10.9 | Rated power frequency withstand voltage phase to earth | kVrms | 460
3.10.10 | Nominal discharge current | kA | 20
3.10.11 | Line discharge class |  | 4
3.10.12 | Rated voltage (Ur) | kV | 180
3.10.13 | Max. continuous operating voltage (Uc) | kV | 144
3.10.14 | Temporary overvoltage withstand capability for 1 sec. | kV
3.10.15 | Temporary overvoltage withstand capability for 10 sec. | kV
3.10.16 | Maximum residual voltage at:
3.10.17 | - 5 kA 8/20 µs | kV
3.10.18 | - 10 kA 8/20 µs | kV
3.10.19 | - 20 kA 8/20 µs | kV
3.10.20 | - 40 kA 8/20 µs | kV
3.10.21 | - 500 A 30/60 µs | kV
3.10.22 | - 1 kA 30/60 µs | kV
3.10.23 | - 2 kA 30/60 µs | kV
3.10.24 | Short circuit strength 0.2 sec. | kA
3.10.25 | Equipped with surge counter with leakage current meter |  | Yes
3.10.26 | Quantity of SF6 gas at rated filling pressure | kg
3.10.27 | Pressure relief device |  | Yes
3.12 | Density guard
3.12.1 | Manufacturer | -
3.12.2 | Place of manufacturing
3.12.3 | Type | -
3.12.4 | Protection class indoor/outdoor | - | IP65
3.12.5 | Amount of contact | -
3.12.6 | Scale (red/green) | - | Yes
3.14 | PD sensors and site testing
3.14.1 | Manufacturer | -
3.14.2 | Place of manufacturing | -
3.14.3 | Type | -
3.14.4 | Test voltage | kV
3.14.5 | Amount of PD sensors
3.14.6 | Document number for description of PD measurement (method and testing equipments including typical test reports) | Document number | Document to be provided with tender.
3.15 | GIS local control cubicles
3.15.1 | Manufacturer | -
3.15.2 | Place of manufacturing | -
3.15.3 | Type |  | free standing or in bay integreated
3.15.4 | Standards
3.15.5 | Material
3.15.6 | Sheet thickness (minimum) | mm | 2
3.15.7 | Minimum paint thickness | µm | 80
3.15.8 | Dimensions (H x W x D) | mm
3.15.9 | Total weight | kg
3.15.10 | Maximum heat emission of one cubicle | W
3.16 | Internal control and signalling cabling of the GIS (between HV bay equipment and local control cubile)
3.16.1 | Control, supervision and interlocking (HV switching equipments)
3.16.2 | Manufacturer
3.16.3 | Place of manufacturing
3.16.4 | Type
3.16.5 | Core amount and size | no/sqmm
3.16.6 | Shielded / if yes, percentage of minimum shielding | Yes/No | ... / %
3.16.7 | Halogen free | Yes/No
3.16.8 | Premanufactured with coded sockets for CB, DE, ES and HSES | Yes/No
3.16.9 | Type of socket (if any)
3.16.10 | Current transformer
3.16.11 | Manufacturer
3.16.12 | Place of manufacturing
3.16.13 | Type
3.16.14 | Core amount and size | no/sqmm
3.16.15 | Shielded / if yes, percentage of minimum shielding | Yes/No | ... / %
3.16.16 | Halogen free | Yes/No
3.16.17 | Voltage transformer
3.16.18 | Manufacturer
3.16.19 | Place of manufacturing
3.16.20 | Type
3.16.21 | Core amount and size | no/sqmm
3.16.22 | Shielded / if yes, percentage of minimum shielding | Yes/No | ... / %
3.16.23 | Halogen free | Yes/No
3.16.24 | Density guard
3.16.25 | Manufacturer
3.16.26 | Place of manufacturing
3.16.27 | Type
3.16.28 | Core amount and size | no/sqmm
3.16.29 | Shielded / if yes, percentage of minimum shielding | Yes/No | ... / %
3.16.30 | Halogen free | Yes/No
3.16.31 | Heating of drive meachism and CT and VT boxes
3.16.32 | Manufacturer
3.16.33 | Place of manufacturing
3.16.34 | Type
3.16.35 | Core amount and size | no/sqmm
3.16.36 | Shielded / if yes, percentage of minimum shielding | Yes/No | ... / %
3.16.37 | Halogen free | Yes/No
3.16.38 | AC/DC ring circuits between local control cubicles
3.16.39 | Manufacturer
3.16.40 | Place of manufacturing
3.16.41 | Type
3.16.42 | Core amount and size | no/sqmm
3.16.43 | Shielded / if yes, percentage of minimum shielding | Yes/No | ... / %
3.16.44 | Halogen free | Yes/No
3.16.45 | Type of cable channels / conduits for bay cabling
3.16.46 | - indoor installation | -
3.16.47 | - outdoor installation | -
3.16.48 | - channels with cover | - | Yes/No
3.17 | Walkways or platforms where needed to reach the drive meachism units for control and operation | - | Yes/No
3.18 | Crane for 220 kV GIS room
3.18.1 | Manufacturer
3.18.2 | Type | - | Overhead travelling
3.18.3 | Capacity | t | ≥ 6
3.18.4 | Operating speed
3.18.5 | - Hoist low/fast | M/min | …/…
3.18.6 | - Trolley travel | M/min
3.18.7 | - Bridge travel | M/min
3.18.8 | Operating power source and terminal voltage
3.18.9 | - Voltage | V AC | 400/230
3.18.10 | - Frequency | Hz | 50
3.18.11 | Dimensions
3.18.12 | - Span | m
3.18.13 | - Length of runway | m
3.18.14 | - Total lift of hook | m
3.18.15 | Crane drive motor
3.18.16 | - Manufacturer
3.18.17 | - Type
3.18.18 | Trolley drive motors
3.18.19 | - Manufactuerer
3.18.20 | - Type
3.18.21 | Operator/Maintenance cage provided with trolley |  | Yes
3.18.22 | Enclosed current collector |  | Yes
3.18.23 | Hoist
3.18.24 | - Manufacturer
3.18.25 | - Type
3.18.26 | - Type of control |  | pendant
3.18.27 | Total required power | KW
3.18.28 | Weights
3.18.29 | - Bridge complete | t
3.18.30 | - Trolley complete | t
3.18.31 | - Runaway complete | t
3.18.32 | Type test Certificates (to be issued by independent laboratory or independent witnessed type test certificate | - | Yes
3.18.33 | Standards for manufacturing and testing | - | to be given
3.19 | Earthing connections for GIS
3.19.1 | Size of main copper earthing conductor for GIS bays | mm2 | ≥ 120
3.19.2 | Size of main copper earthing conductor for local control cubicles | mm2 | ≥ 16
3.20 | Steel structures for GIS
3.20.1 | Manufacturer | -
3.20.2 | Place of manufacture | -
3.20.3 | Applicable standard | -
3.20.4 | Material | -
3.20.5 | Factor of safety in calculation | -
3.20.6 | Galvanization thickness:
3.20.7 | - Steel sections thicker than 5 mm | μm
3.20.8 | - Steel sections 2 mm-5 mm μm | μm
3.20.9 | - Bolts and nuts μm | μm
3.20.10 | Bolts and nuts:
3.20.11 | - Securing with plain and spring washers | yes/no
3.20.12 | - yes/no
3.20.13 | - Minimum quality
3.20.14 | Tests according to relevant standards and Employer's Requirements | yes/no | yes
3.21 | Gas service cart | -
3.21.1 | Manufacturer | -
3.21.2 | Place of manufacture | -
3.21.3 | Model designation | -
3.21.4 | Type of gas storage | - | cylinder or tank
3.21.5 | Size of gas strorage | kg | ≥ 200
3.21.6 | Final recovery vacuum | mbar | < 1
3.21.7 | Evacuation time for biggest gas compartment | h | < 2
3.21.8 | Revocerey time for biggest gas compartment | h | < 8
3.21.9 | Including specified and necessaey additives (filters, couplings, valves, manifolds, hoses etc.) | - | yes
3.21.10 | Minimum length of the SF6 gas hoses | m
3.21.11 | Supply voltage 400/230 V 50 Hz | - | 3-phase
3.21.12 | Maximum 3-phase current | A
3.22 | SF6 gas filling cart with wire-braided hoses
3.22.1 | Manufacturer | -
3.22.2 | Place of manufacture | -
3.22.3 | Model designation | -
3.22.4 | Hose reel | - | yes
3.22.5 | Amount of different bottle connections | - | ≥ 2
3.22.6 | Self closing couplings | - | yes
3.22.7 | Couplings suitable for all used filling ports of GIS | - | yes
3.22.8 | Hose lenght | m | ≥ 6
3.23 | Analizer for gas meassurement
3.23.1 | Manufacturer | -
3.23.2 | Place of manufacture | -
3.23.3 | Model designation | -
3.23.4 | Applicable standard | - | IEC 62271-4
3.23.5 | Measuring functions:
3.23.6 | - Dew point meter | - | yes
3.23.7 | - SF6 percentage measuring | - | yes
3.23.8 | - Analyser for by-products | - | yes
3.23.9 | - SF6 pressure gauge | - | yes
3.23.10 | - Thermometer | - | yes
3.23.11 | Suitable connection additives for all used GIS filling ports | - | yes
3.24 | Portable SF6 gas leakage detector in case
3.24.1 | Manufacturer
3.24.2 | Type
3.25 | Density guard testing device in a case
3.25.1 | Manufacturer
3.25.2 | Type
3.25.3 | Including calibrated manometer and necessary additives | - | yes
3.26 | Precision gauge with hose in transport case
3.26.1 | Manufacturer | -
3.26.2 | Type | -
3.26.3 | Indicating range | kPa | 0 - 1000
3.26.4 | Class | - | 0.6
3.26.5 | Teflon hose (length ≥1m) with additives | - | yes
3.27 | Tests according to relevant standards and Employer's Requirements for service and testing equipments |  | yes
3.28 | SF6 gas
3.28.1 | Manufacturer | -
3.28.2 | Applicable standard | - | IEC 60376
3.28.3 | Amount as spare for the use of Employer | kg
3.29 | Documentation and wall boards for 220 kV GIS
3.29.1 | As specified in local language | - | yes
3.29.2 | Wall boards/charts as specified in local language | - | yes

## 4. 132 kV GIS
Technical Data Sheets
BIDDER’S / CONTRACTOR’S GUARANTEED DATA |  | Unit | Data required | Data offered
No. | Description
4 | 132 kV Gas Insulated Switchgear (GIS)
4.1 | General
4.1.1 | Manufacturer | -
4.1.2 | Place of manufacture | -
4.1.3 | Model designation | -
4.1.4 | Type | - | Metal enclosed, gas insulated GIS- indoor
4.1.5 | Applicable standard | - | IEC 62271-203, 62271-1, 60270, 60376, 60480
4.1.6 | Nominal voltage of system | kVrms | 132
4.1.7 | Rated voltage of system | kVrms | 145
4.1.8 | Rated frequency | Hz | 50
4.1.9 | Rated short-duration power frequency withstand voltage:
4.1.10 | - Common Value | kVrms | 275
4.1.11 | - Across the isolating distance | kVrms | 315
4.1.12 | Rated lightning impulse withstand voltage:
4.1.13 | - Phase to earth | kVpeak | 650
4.1.14 | - Across the isolating distance | kVpeak | 750
4.1.15 | Rated short-time withstand current (3s) | kA | 40
4.1.16 | Rated peak withstand current | kA | 100
4.1.17 | Rated current (busbar) | A | 2500
4.1.18 | Rated current (bus coupler) | A | 2500
4.1.19 | Rated current (feeders) | A | 2500
4.1.20 | Type of busbars | - | Double
4.1.21 | Type of enclosure | - | Three phase enclosures
4.1.22 | Material of enclosure for:
4.1.23 | - Circuit breaker | - | Al
4.1.24 | - Busbars | - | Al
4.1.25 | - Other compartments | - | Al
4.1.26 | Applicable standard for SF6 pressurized enclosures | - | EN 50052, 50064, 50068, 50069, 50089
4.1.27 | Minimum safety factor for switchgear (GIS housings/steel supports) | - | ≥ 2,5
4.1.28 | Seismic factor according to IEEE 693 figure A.1 | g | 0,5
4.1.29 | Suitability for the site climate/temperature range: | °C | 0 - 40
4.1.30 | Material and cross-section of bus bar conductor | .../ mm2
4.1.31 | Material and cross-section of feeder bus-duct conductor | .../ mm2
4.1.32 | Material of contacts (indicate bi-metallic where used) | - | Cu/Ag
4.1.33 | Type of contact | - | Tulip/plug-in
4.1.34 | Surface treatment of GIS housings:
4.1.35 | - Indoor paint / layer thickness | RAL / µm
4.1.36 | - Outdoor paint / layer thickness | RAL / µm
4.1.37 | - Flange treatment (outdoor) | - | Add number of technical description
4.1.38 | Colour of partition insulators | RAL
4.1.39 | Colour of local control cubicle | RAL
4.1.40 | Minimum subdivision of GIS switchgear (partition):
4.1.41 | - Busbars per each feeder | - | Yes
4.1.42 | - Busbar isolator | - | Yes
4.1.43 | - Circuit breaker | - | Yes
4.1.44 | - Feeder disconnector and cable end unit | - | Yes
4.1.45 | - Voltage transformer | - | Yes
4.1.46 | - Current transformer | - | Yes/No
4.1.47 | - Surge arrester (if any) | - | Yes
4.1.48 | - Max. lenght/volume of gas insulated bus duct | Meter/Litre | …/…
4.1.49 | Maximum size of gas compartment | Litre
4.1.50 | Maximum evaquation time of gas compartment | hrs | < 2
4.1.51 | Method of compensation of expansion and contraction:
4.1.52 | - For busbar conductors | - | Expansion
4.1.53 | - For busbar enclosures | - | Expansion
4.1.54 | Type/ material of pressure relief device | - | Rupture disc / …
4.1.55 | Rupturing pressure of pressure relief device (circuit breaker/others) | MPa | …/…
4.1.56 | Type of filter employed for moisture absorption | - | Molecular Sieve
4.1.57 | Design lifetime of moisture absorbent | Years | > 10
4.1.58 | Total mass of switchgear / haviest transportation unit | kg | …/…
4.1.59 | Size of maximum transportation unit (L x W x H) | m
4.1.60 | Mass of heaviest single component to be handled during erection | kg
4.1.61 | Mass of heaviest single indoor component to be handled during erection with the indoor crane | kg
4.1.62 | Bay width (centre to centre) | m
4.1.63 | Indoor foorprint of initial GIS | m x m
4.1.64 | Indoor foortprint including extension | m x m
4.1.65 | Minimum indoor crane hook height | m
4.1.66 | Indoor crane lifting force | t | ≥ 6
4.1.67 | Crane with 2 speeds suitable for GIS installation | - | Yes
4.1.68 | Applicable standard for new SF6 gas | - | IEC 60376
4.1.69 | Density of gas in:
4.1.70 | - Circuit breaker compartment | g/l
4.1.71 | - Other than circuit breaker compartment | g/l
4.1.72 | Rated filling pressure at 20ºC (CB/others) | MPa | … / …
4.1.73 | 1st alarm pressure at 20ºC (CB/others) | MPa | … / …
4.1.74 | Circuit breaker blocking pressure at 20ºC (Close/Open) | MPa | … / …
4.1.75 | Maximum SF6 leakage rate | % / year | < 0,1
4.1.76 | Design pressure of enclosures (circuit breaker/ others) | MPa | …/…
4.1.77 | Type test presure of enclosures (circuit breaker/others | MPa | …/…
4.1.78 | Routine test pressure of casted enclosures (circuit breaker/others) | MPa | …/…
4.1.79 | Routine test pressure of welded enclosures (circuit breaker/others) | MPa | …/…
4.1.80 | Design pressure of gas tight barrier insulator | MPa
4.1.81 | Routine test pressure of gas tight barrier insulator | MPa
4.1.82 | Withstand voltage at SF6 gas atmospheric pressure | kV | 145
4.1.83 | Minimum gas service period | years | > 10
4.1.84 | Document number showing maximum allowable dewpoint depending on temperature for different gas filling/compartments | - | to be provided with Tender
4.1.85 | Recommended inspection/maintenance intervals | years
4.1.86 | Neutral earthing | - | solidly
4.1.87 | Document number showing the Inspection and Test Plan for the complete GIS scope of supply including FAT. | - | to be provided with Tender
4.2 | Circuit breaker
4.2.1 | Manufacturer | -
4.2.2 | Place of manufacture | -
4.2.3 | Model designation | -
4.2.4 | Type | - | Self-blast pressure buffer,SF6
4.2.5 | Applicable standard | - | IEC 62271-1 lEC 62271-203, IEC 62271-100
4.2.6 | Type of quenching medium |  | SF6
4.2.7 | Interrupter units per pole | pcs | 1
4.2.8 | Rated voltage | kV | 145
4.2.9 | Rated short-duration power frequency withstand voltage:
4.2.10 | - Common Value | kVrms | 275
4.2.11 | - Across the isolating distance | kVrms | 315
4.2.12 | Rated lightning impulse withstand voltage:
4.2.13 | - Common Value | kVpeak | 650
4.2.14 | - Across the isolating distance | kVpeak | 750
4.2.15 | Rated frequency | Hz | 50
4.2.16 | Number of phases | - | 3
4.2.17 | Rated current (bus coupler/feeders) | A | 2500/2500
4.2.18 | Rated short-time withstand current (3s) | kA | 40
4.2.19 | Rated peak withstand current | kA | 100
4.2.20 | Rated making current | kA | 100
4.2.21 | Rated cable charging breaking current | A
4.2.22 | Maximum capacitive breaking current: | A | to IEC 62271-100
4.2.23 | - Rated line charging breaking current | A | 50
4.2.24 | - Rated cable charging breaking current | A | 160
4.2.25 | - Rated Single/Back to Back Capacitor bank breaking current | A | 400
4.2.26 | - Rated single capacitor bank breaking current | A | 400
4.2.27 | Rated breaking current asymmetrical | kA
4.2.28 | - %dc | %dc
4.2.29 | Rated breaking current under out-of-phase conditions | kA
4.2.30 | Terminal fault | kpp / p.u. | 1,3
4.2.31 | Short-Line-fault | kpp / p.u. | 1
4.2.32 | Out-of-phase | kpp / p.u. | 2
4.2.33 | Rated small inductive/reactor breaking currents of: |  | to IEC 62271-100
4.2.34 | - Small inductive loads | A
4.2.35 | - Reactor | A
4.2.36 | Maximum overvoltage factor when interrupting rated line/cable/ capacitor bank charging currents | pu | (2.5 or) restrike free
4.2.37 | Maximum overvoltage factor when switching small inductive/reactor currents | pu | 2.5
4.2.38 | Number of tripping coils | - | 2
4.2.39 | Number of closing coils | - | 1
4.2.40 | Type of operation | - | OHL feeders: single phase / other feeders three phase
4.2.41 | Rated operating sequence | - | 0 - 0,3 s - CO - 3 min - CO
4.2.42 | Opening time | ms | < 30
4.2.43 | Breaking time | ms | < 50
4.2.44 | Closing time | ms | < 60
4.2.45 | Dead time | ms | 300
4.2.46 | Maximum time interval between opening of first and last phase of three phase circuit breakers | ms | ≤ 3
4.2.47 | Closing time from energization of close coil to latching of circuit breaker in fully closed position | ms
4.2.48 | Making time (energization of close coil to contact touch):
4.2.49 | - Without current | ms
4.2.50 | - 100% making current | ms
4.2.51 | Minimum time from extinction of main arc to contact make during auto-reclosing duty | ms | 300
4.2.52 | Mechanical life of circuit breaker | - | M2
4.2.53 | Electrical contact life in number of operations at:
4.2.54 | - Rated current- 2500/2500A | - | 10 000
4.2.55 | - Fault current - 40 kA | - | 9
4.2.56 | - Cumulative ampere rating | -
4.2.57 | Number of current interrupting break units in series per phase | - | One
4.2.58 | Type of operating mechanism | - | Spring-charged
4.2.59 | Type of power device (motor-charged)
4.2.60 | - For closing | - | Spring-charged
4.2.61 | - For opening | - | Spring-charged
4.2.62 | Motor power | W
4.2.63 | Hand operating facility | - | Yes
4.2.64 | Hand charging facility | - | Yes
4.2.65 | Manual spring release | - | Yes
4.2.66 | Mechanical on/off indicator | - | Yes
4.2.67 | Mechanical spring charge/discharge indication | - | Yes
4.2.68 | Charging time | s
4.2.69 | Number of tripping coils | - | 2
4.2.70 | Number of closing coils | - | 1
4.2.71 | Rated power of close coil | W
4.2.72 | Rated power of trip coil | W
4.2.73 | Number of auxiliary contacts (NO/NC) | -
4.2.74 | Mechanical endurance | - | M2
4.2.75 | Capasitive current switching | - | C2
4.2.76 | Nominal control and operating voltage | V DC | 220
4.2.77 | Nominal heater voltage | V AC | 230
4.2.78 | Total load of heaters for circuit breaker | W
4.2.79 | Total SF6 gas weight of circuit breaker | kg
4.2.80 | Total weight of the circuit breaker (three phases) | kg
4.2.81 | Emergency Trip Facility during failure of DC supply | - | Yes
4.2.82 | Protection class of drive mechanism box | - | IP55
4.3 | Disconnectors
4.3.1 | Manufacturer | -
4.3.2 | Place of manufacturing | -
4.3.3 | Model designation | -
4.3.4 | Type | - | three position switch
4.3.5 | Applicable standard | - | IEC 62271-1 IEC 62271-102 62271-203
4.3.6 | Type of operating mechanism | - | Motor & Manual
4.3.7 | Rated voltage | kV | 132
4.3.8 | Rated current bus bar, bus coupler | A | 2500
4.3.9 | Rated current feeders | A | 2500
4.3.10 | Rated lightning impulse withstand voltage
4.3.11 | - Common Value | kVpeak | 650
4.3.12 | - Across the isolating distance | kVpeak | 750
4.3.13 | Rated power frequency withstand voltage
4.3.14 | - Common Value | kVrms | 275
4.3.15 | - Across the isolating distance | kVrms | 315
4.3.16 | Rated frequency | Hz | 50
4.3.17 | Rated short time withstand current (3s) | kA | 40
4.3.18 | Rated short-circuit peak withstand current | kA | 100
4.3.19 | Maximum capacitive current that can be interrupted by the isolator | A
4.3.20 | Total time from initiation of opening operation to isolator in fully open position | s
4.3.21 | Time from contact separation to extinct of capacitive arc | s
4.3.22 | Total time from initiation of opening operation to time when isolator gap can withstand phase voltage | s
4.3.23 | Bus-transfer current switching ability:
4.3.24 | - bus-transfer current | A | 1600
4.3.25 | - bus transfer voltage | V | 10
4.3.26 | Hand operating facility | - | Yes
4.3.27 | Locking arrangement in on/off position | - | Yes
4.3.28 | Number of auxiliary contacts (NO/NC/others) | -
4.3.29 | Nominal control and operating voltage | V DC | 220
4.3.30 | Automatic isolation of control supplies when DS locked in open position | - | Yes
4.3.31 | Accessibility to operating mechanism from ground level or catwalk | - | Yes
4.3.32 | Nominal heater voltage | V AC | 230
4.3.33 | Total load of heaters for isolator | W
4.3.34 | Rated motor power | W
4.3.35 | Total mass of three phase disconnector complete | kg
4.3.36 | Contact type | - | Tulip/plug-in
4.3.37 | Mechanical endurance | - | M2
4.3.38 | Viewing windows |  | Yes
4.3.39 | Protection class of drive mechanism box | - | IP 55
4.4 | Maintenance earthing switch
4.4.1 | Manufacturer | -
4.4.2 | Place of manufacturing | -
4.4.3 | Model designation | -
4.4.4 | Type | - | three position switch
4.4.5 | Type of operating mechanism | - | Motor & Manual
4.4.6 | Applicable standard | - | IEC 62271-1 IEC 62271-102 62271-203
4.4.7 | Rated voltage | kV | 145
4.4.8 | Rated lightning impulse withstand voltage phase to earth | kVpeak | 650
4.4.9 | Rated power frequency withstand voltage phase to earth | kVrms | 275
4.4.10 | Rated frequency | Hz | 50
4.4.11 | Rated short time withstand current (3s) | kA | 40
4.4.12 | Rated short-circuit peak withstand current | kA | 100
4.4.13 | Total opening time | s
4.4.14 | Total closing time | s
4.4.15 | Hand operating facility | - | Yes
4.4.16 | Locking arrangement in on/off position | - | Yes
4.4.17 | Number of auxiliary contacts (NO/NC) | -
4.4.18 | Nominal control and operating voltage | V DC | 220
4.4.19 | Automatic isolation of control supplies when DS locked in open position | - | Yes
4.4.20 | Accessibility to operating mechanism from ground level or catwalk | - | Yes
4.4.21 | Nominal heater voltage | V AC | 230
4.4.22 | Total load of heaters for isolator | W
4.4.23 | Rated motor power | W
4.4.24 | Rated power of operation coil | W
4.4.25 | Rated insulation of brought out connection | kV | 10
4.4.26 | Total mass of maintenance earthing switch | kg
4.4.27 | Contact type |  | Tulip/plug-in
4.4.28 | Viewing windows |  | Yes
4.4.29 | Protection class of drive mechanism box | - | IP 55
4.5 | High speed earthing switch
4.5.1 | Manufacturer | -
4.5.2 | Place of manufacturing | -
4.5.3 | Model designation | -
4.5.4 | Type | - | attached unit
4.5.5 | Type of operating mechanism | - | Motor & Manual spring charged
4.5.6 | Applicable standard | - | IEC 62271-1 IEC 62271-102 62271-203
4.5.7 | Rated voltage | kV | 145
4.5.8 | Rated lightning impulse withstand voltage phase to earth | kVpeak | 650
4.5.9 | Rated power frequency withstand voltage phase to earth | kVrms | 275
4.5.10 | Rated frequency | Hz | 50
4.5.11 | Rated short time withstand current (3s) | kA | 40
4.5.12 | Rated short-circuit peak withstand current | kA | 100
4.5.13 | Mechanical endurance / Number of making operations at rated making current (40kA) |  | E1
4.5.14 | Rated capacitive symmetrical making current | A
4.5.15 | Rated inductive symmetrical making current | A
4.5.16 | Total time from initiation of opening operation to earth switch in fully open position | s
4.5.17 | Making time | ms
4.5.18 | Charging time | s
4.5.19 | Hand operating facility | - | Yes
4.5.20 | Locking arrangement in on/off position | - | Yes
4.5.21 | Number of auxiliary contacts (NO/NC) | -
4.5.22 | Nominal control and operating voltage | V DC | 220
4.5.23 | Automatic isolation of control supplies when HES locked in open position | - | Yes
4.5.24 | Accessibility to operating mechanism from ground level or catwalk | - | Yes
4.5.25 | Nominal heater voltage | V AC | 230
4.5.26 | Total load of heaters for isolator | W
4.5.27 | Rated motor power | W
4.5.28 | Rated power of operation coil | W
4.5.29 | Rated insulation of brought out connection | kV | 10
4.5.30 | Total mass of high speed earthing switch | kg
4.5.31 | Contact type |  | Tulip/plug-in
4.5.32 | Viewing windows |  | Yes
4.5.33 | Protection class of drive mechanism box | - | IP 55
4.6 | Current transformer |  | integrated
4.6.1 | Manufacturer | -
4.6.2 | Place of manufacturing | -
4.6.3 | Type | -
4.6.4 | Applicable standard | - | IEC 61869-1 IEC 61869-2 IEC 62271-1 IEC 62271-203
4.6.5 | Rated voltage | kV | 145
4.6.6 | Rated power frequency withstand voltage phase to earth (GIS) | kV | 275
4.6.7 | Rated lightning impulse withstand voltage Phase to earth (GIS) |  | 650
4.6.8 | Rated power frequency voltage of secondary winding | kV | 3
4.6.9 | Inter-turn test | kVpeak | 4.5
4.6.10 | Rated frequency | Hz | 50
4.6.11 | Rated short-time withstand current (3 s) | kA | 40
4.6.12 | Rated short-circuit peak withstand current | kA | 100
4.6.13 | Rated extended primary current in percentage of rated primary current | % | 120
4.6.14 | 220/132 kV Power-transformer bay current transformer
4.6.14.1 | - number of cores | -
4.6.14.2 | Metering |  | 1
4.6.14.3 | Measuring |  | 1
4.6.14.4 | Protetction |  | 2
4.6.14.5 | Busbar Protection |  | 1
4.6.14.6 | - Ratio
4.6.14.7 | Metering / measuring / protection | A | 400-600-800/1
4.6.14.8 | Busbar Protection | A | 2500/1
4.6.14.9 | - Class
4.6.14.10 | Metering | - | 0.2S
4.6.14.11 | Measuring | - | 0,5 FS 5
4.6.14.12 | Protetction | - | 5P20
4.6.14.13 | Busbar Protection | - | 5P20
4.6.14.14 | - Rated output (burden to be 25-100 % rated burden)
4.6.14.15 | Metering | VA | 15
4.6.14.16 | Measuring | VA | 15
4.6.14.17 | Protetction | VA | 30
4.6.14.18 | Busbar Protection | VA | 30
4.6.15 | Overhead line bay current transformer
4.6.15.1 | - number of cores | -
4.6.15.2 | Metering |  | 1
4.6.15.3 | Measuring |  | 1
4.6.15.4 | Protetction |  | 2
4.6.15.5 | Busbar Protection |  | 1
4.6.15.6 | - Ratio
4.6.15.7 | Metering / measuring / protection | A | 1000-1250-1500/1
4.6.15.8 | Busbar Protection | A | 2500/1
4.6.15.9 | - Class
4.6.15.10 | Metering | - | 0.2S
4.6.15.11 | Measuring | - | 0,5 FS 5
4.6.15.12 | Protetction | - | 5P20
4.6.15.13 | Busbar Protection | - | 5P20
4.6.15.14 | - Rated output (burden to be 25-100 % rated burden)
4.6.15.15 | Metering | VA | 15
4.6.15.16 | Measuring | VA | 15
4.6.15.17 | Protetction | VA | 30
4.6.15.18 | Busbar Protection | VA | 30
4.6.16 | 132/33 kV Transformer bay current transformer
4.6.16.1 | - number of cores | -
4.6.16.2 | Metering |  | 1
4.6.16.3 | Measuring |  | 1
4.6.16.4 | Protetction |  | 2
4.6.16.5 | Busbar Protection |  | 1
4.6.16.6 | - Ratio
4.6.16.7 | Metering / measuring / protection | A | 150-300-600/1
4.6.16.8 | Busbar Protection | A | 2500/1
4.6.16.9 | - Class
4.6.16.10 | Metering | - | 0.2S
4.6.16.11 | Measuring | - | 0,5 FS 5
4.6.16.12 | Protetction | - | 5P20
4.6.16.13 | Busbar Protection | - | 5P20
4.6.16.14 | - Rated output (burden to be 25-100 % rated burden)
4.6.16.15 | Metering | VA | 15
4.6.16.16 | Measuring | VA | 15
4.6.16.17 | Protetction | VA | 30
4.6.16.18 | Busbar Protection | VA | 30
4.6.17 | Bus coupler bay current transformer (both sides)
4.6.17.1 | - number of cores | -
4.6.17.2 | Metering |  | -
4.6.17.3 | Measuring |  | 1
4.6.17.4 | Protetction |  | 1
4.6.17.5 | Busbar Protection |  | 1
4.6.17.6 | - Ratio
4.6.17.7 | Metering / measuring / protection | A | 1000-1500-2500/1
4.6.17.8 | Busbar Protection | A | 2500/1
4.6.17.9 | - Class
4.6.17.10 | Metering | - | -
4.6.17.11 | Measuring | - | 0,5 FS 5
4.6.17.12 | Protetction | - | 5P20
4.6.17.13 | Busbar Protection | - | 5P20
4.6.17.14 | - Rated output (burden to be 25-100 % rated burden)
4.6.17.15 | Metering | VA | -
4.6.17.16 | Measuring | VA | 15
4.6.17.17 | Protetction | VA | 30
4.6.17.18 | Busbar Protection | VA | 30
4.7 | Inductive voltage transformer (bus bars)
4.7.1 | Manufacturer
4.7.2 | Place of manufacturing
4.7.3 | Type |  | Inductive, SF6 gas insulated
4.7.4 | Applicable standard |  | IEC 62271-1 IEC 62271-203 IEC 61869-1 IEC 61869-3
4.7.5 | Separated from the bus bar with disconnector |  | Yes
4.7.6 | Rated primary voltage | kV | 145
4.7.7 | Rated frequency | HZ | 50
4.7.8 | Rated lightning impulse phase to earth | kVpeak | 650
4.7.9 | Rated power frequency withstand voltage phase to earth | kVrms | 275
4.7.10 | Maximum permissible partial discharge level Um | pC | 10
4.7.11 | Maximum permissible partial discharge level 1.2Um/√3 | pC | 5
4.7.12 | Method of suppressing Ferro-resonance phenomena | -
4.7.13 | Bus bar voltage transformer
4.7.14 | - Number of secondary | - | 2
4.7.15 | - Rated transformation ratio | kV | 132/√3 /0.11/√3/ 0.11/√3
4.7.16 | - Rated accuracy class
4.7.17 | Secondary winding 1 | - | 0,2 / 3P
4.7.18 | Secondary winding 2 | - | 0,2 / 3P
4.7.19 | - Rated output
4.7.20 | Secondary winding 1 | VA | 100
4.7.21 | Secondary winding 2 | VA | 100
4.7.22 | - Mass of voltage transformer | kg
4.7.23 | - Quantity of SF6 gas at rated filling pressure | kg
4.7.24 | Rated voltage factor
4.7.25 | - continuous |  | 1,2
4.7.26 | - 30 s |  | 1,5
4.8 | GIS cabel end unit housing
4.8.1 | Manufacturer | -
4.8.2 | Place of manufacturing | -
4.8.3 | Type | - | plug-in
4.8.4 | Applicable standard | - | IEC 62271-1 IEC 62271-203 IEC 62271-209
4.8.5 | Rated voltage of main circuit | kV | 145
4.8.6 | Rated lightning impulse withstand voltage phase to earth of main circuit | kV | 650
4.8.7 | Rated power frequency withstand voltage phase to earth of main circuit | kV | 275
4.8.8 | Cable HV test withstand capability (maximum cable test AC voltage) | kV
4.8.9 | Rated frequency | Hz | 50
4.8.10 | Type of cable | - | XLPE
4.8.11 | Cable cross section (minimum) | mm2 | 300
4.8.12 | Quantity of SF6 gas at rated filling pressure | kg
4.8.13 | Total mass of three phase cable end unit box | kg
4.8.14 | Type of cable socket | -
4.8.15 | Manufacturer of the socket | -
4.9 | Bus ducts
4.9.1 | Manufacturer
4.9.2 | Place of manufacturing
4.9.3 | Type
4.9.4 | Applicable standard |  | IEC 62271-1 IEC 62271-203
4.9.5 | Common enclosed phases | pcs | 3
4.9.6 | Rated current at max. ambient temperature and sun radiation | A | 1500 A at 50 ⁰C
4.9.7 | Inductance | H/m
4.9.8 | Capacitance | pF/m
4.9.9 | Resistance of enclosure | Ohm/m
4.9.10 | Resistance of conductor | Ohm/m
4.9.11 | Surge impedance | Ohm
4.9.12 | Quantity of SF6 gas at rated filling pressure:
4.9.13 | - shortest bus duct | kg
4.9.14 | - maximum gas compartment | kg
4.9.15 | - longest complete feeder bus duct | kg
4.10 | GIS SF6 air bushing
4.10.1 | Manufacturer | -
4.10.2 | Place of manufacturing | -
4.10.3 | Type | -
4.10.4 | Model designation | -
4.10.5 | Applicable standard | - | IEC 62271-1 IEC 62271-203 IEC 60137 IEC 61643
4.10.6 | Type of internal insulation |  | Gas-insulated
4.10.7 | Type of external insulation |  | Composite
4.10.8 | Shed profile | - | alternating
4.10.9 | Highest voltage for equipment Um | kV | 145
4.10.10 | Rated phase-to-earth voltage |  | 0,8 x Um
4.10.11 | Rated lightning impulse withstand voltage | kVpeak | 650
4.10.12 | Power-frequency withstand voltage | kVrms | 275
4.10.13 | Rated current at max. ambient temperature and sun radiation | A | 1500 A at 50 ⁰C
4.10.14 | Rated short time current (3s) | kA | 40
4.10.15 | Rated dynamic current | kA | 100
4.10.16 | Inner filling of the bushing |  | SF6
4.10.17 | Rated design pressure | MPa
4.10.18 | SF6 filling; pressure at 20⁰C | Mpa
4.10.19 | Min. SF6 service pressure | MPa
4.10.20 | Routine test pressure | MPa
4.10.21 | Bursting pressure | MPa
4.10.22 | Max. leakage rate at filling pressure | % | ≤ 0,1
4.10.23 | Minimum Unified Specific Creepage Distance (USCD) | mm/kV | 43,3
4.10.24 | Current conductor material | -
4.10.25 | Current conductor diameter | mm
4.10.26 | Cantilever test load | N
4.10.27 | Cantilever opertion load | N
4.10.28 | Type of line termination | -
4.10.29 | Seismic acceleration according to IEEE 693 figure A.1 | g | 0,5
4.10.30 | Quantity of SF6 gas (if any) at rated filling pressure | kg
4.10.31 | Quantity of SF6 gas (if any) at rated filling pressure | kg
4.10.32 | Weight | kg
4.11 | GIS lightning arrester - gapless zinc-oxide type (if any)
4.11.1 | Manufacturer | -
4.11.2 | Place of manufacturing
4.11.3 | Type | - | MO
4.11.4 | Applicable standard |  | IEC 60099-4 IEC 60099-5 IEC 62271-1 IEC 62271-203
4.11.5 | Nominal voltage | kVrms | 110
4.11.6 | Rated voltage | kVrms | 123
4.11.7 | Rated frequency | Hz | 50
4.11.8 | Rated lightning impulse withstand voltage phase to earth | kVpeak | 550
4.11.9 | Rated power frequency withstand voltage phase to earth | kVrms | 230
4.11.10 | Nominal discharge current | kA | 20
4.11.11 | Line discharge class |  | 4
4.11.12 | Rated voltage (Ur) | kV | 108
4.11.13 | Max. continuous operating voltage (Uc) | kV | 86
4.11.14 | Temporary overvoltage withstand capability for 1 sec. | kV
4.11.15 | Temporary overvoltage withstand capability for 10 sec. | kV
4.11.16 | Maximum residual voltage at:
4.11.17 | - 5 kA 8/20 µs | kV
4.11.18 | - 10 kA 8/20 µs | kV
4.11.19 | - 20 kA 8/20 µs | kV
4.11.20 | - 40 kA 8/20 µs | kV
4.11.21 | - 500 A 30/60 µs | kV
4.11.22 | - 1 kA 30/60 µs | kV
4.11.23 | - 2 kA 30/60 µs | kV
4.11.24 | Short circuit strength 0.2 sec. | kA
4.11.25 | Equipped with surge counter with leakage current meter |  | Yes
4.11.26 | Quantity of SF6 gas at rated filling pressure | kg
4.11.27 | Pressure relief device |  | Yes
4.12 | Density guard
4.12.1 | Manufacturer | -
4.12.2 | Place of manufacturing | -
4.12.3 | Type | -
4.12.4 | Protection class indoor/outdoor | - | IP65
4.12.5 | Amount of contact | -
4.12.6 | Scale (red/green) | - | Yes
4.13 | PD sensors and site testing
4.13.1 | Manufacturer | -
4.13.2 | Place of manufacturing | -
4.13.3 | Type | -
4.13.4 | Test voltage | kV
4.13.5 | Amount of PD sensors
4.13.6 | Document number for description of PD measurement (method and testing equipments including typical test reports) | Document number | Document to be provided with tender.
4.14 | GIS local control cubicles
4.14.1 | Manufacturer | -
4.14.2 | Place of manufacturing | -
4.14.3 | Type |  | in bay integreated
4.14.4 | Standards
4.14.5 | Material
4.14.6 | Sheet thickness (minimum) | mm | 2
4.14.7 | Minimum paint thickness | µm | 80
4.14.8 | Dimensions (H x W x D) | mm
4.14.9 | Total weight | kg
4.14.10 | Maximum heat emission of one cubicle | W
4.15 | Internal control and signalling cabling of the GIS (between HV bay equipment and local control cubile)
4.15.1 | Control, supervision and interlocking (HV switching equipments)
4.15.2 | Manufacturer
4.15.3 | Place of manufacturing
4.15.4 | Type
4.15.5 | Core amount and size | no/sqmm
4.15.6 | Shielded / if yes, percentage of minimum shielding | Yes/No | ... / %
4.15.7 | Halogen free | Yes/No
4.15.8 | Premanufactured with coded sockets for CB, DE, ES and HSES | Yes/No
4.15.9 | Type of socket (if any)
4.15.10 | Density guard
4.15.11 | Manufacturer
4.15.12 | Place of manufacturing
4.15.13 | Type
4.15.14 | Core amount and size | no/sqmm
4.15.15 | Shielded / if yes, percentage of minimum shielding | Yes/No | ... / %
4.15.16 | Halogen free | Yes/No
4.15.17 | Current transformer
4.15.18 | Manufacturer
4.15.19 | Place of manufacturing
4.15.20 | Type
4.15.21 | Core amount and size | no/sqmm
4.15.22 | Shielded / if yes, percentage of minimum shielding | Yes/No | ... / %
4.15.23 | Halogen free | Yes/No
4.15.24 | Voltage transformer
4.15.25 | Manufacturer
4.15.26 | Place of manufacturing
4.15.27 | Type
4.15.28 | Core amount and size | no/sqmm
4.15.29 | Shielded / if yes, percentage of minimum shielding | Yes/No | ... / %
4.15.30 | Halogen free | Yes/No
4.15.31 | Density guard
4.15.32 | Manufacturer
4.15.33 | Place of manufacturing
4.15.34 | Type
4.15.35 | Core amount and size | no/sqmm
4.15.36 | Shielded / if yes, percentage of minimum shielding | Yes/No | ... / %
4.15.37 | Halogen free | Yes/No
4.15.38 | Heating of drive meachism and CT and VT boxes
4.15.39 | Manufacturer
4.15.40 | Place of manufacturing
4.15.41 | Type
4.15.42 | Core amount and size | no/sqmm
4.15.43 | Shielded / if yes, percentage of minimum shielding | Yes/No | ... / %
4.15.44 | Halogen free | Yes/No
4.15.45 | AC/DC ring circuits between local control cubicles
4.15.46 | Manufacturer
4.15.47 | Place of manufacturing
4.15.48 | Type
4.15.49 | Core amount and size | no/sqmm
4.15.50 | Shielded / if yes, percentage of minimum shielding | Yes/No | ... / %
4.15.51 | Halogen free | Yes/No
4.15.52 | Type of cable channels / conduits for bay cabling
4.15.53 | - indoor installation | -
4.15.54 | - outdoor installation | -
4.15.55 | - channels with cover | - | Yes/No
4.16 | Walkways or platforms where needed to reach the drive meachism units for control and operation | - | Yes/No
4.17 | Crane for 132 kV GIS room
4.17.1 | Manufacturer
4.17.2 | Type | - | Overhead travelling
4.17.3 | Capacity | t | ≥ 6
4.17.4 | Operating speed
4.17.5 | - Hoist low/fast | M/min | …/…
4.17.6 | - Trolley travel | M/min
4.17.7 | - Bridge travel | M/min
4.17.8 | Operating power source and terminal voltage
4.17.9 | - Voltage | V AC | 400/230
4.17.10 | - Frequency | Hz | 50
4.17.11 | Dimensions
4.17.12 | - Span | m
4.17.13 | - Length of runway | m
4.17.14 | - Total lift of hook | m
4.17.15 | Crane drive motor
4.17.16 | - Manufacturer
4.17.17 | - Type
4.17.18 | Trolley drive motors
4.17.19 | - Manufactuerer
4.17.20 | - Type
4.17.21 | Operator/Maintenance cage provided with trolley |  | Yes
4.17.22 | Enclosed current collector |  | Yes
4.17.23 | Hoist
4.17.24 | - Manufacturer
4.17.25 | - Type
4.17.26 | - Type of control |  | pendant
4.17.27 | Total required power | KW
4.17.28 | Weights
4.17.29 | - Bridge complete | t
4.17.30 | - Trolley complete | t
4.17.31 | - Runaway complete | t
4.17.32 | Type test Certificates (to be issued by independent laboratory or independent witnessed type test certificate | - | Yes
4.17.33 | Standards for manufacturing and testing | - | to be given
4.17.34
4.17.35 | Earthing connections for GIS
4.17.36 | Size of main copper earthing conductor for GIS bays | mm2 | ≥ 120
4.17.37 | Size of main copper earthing conductor for local control cubicles | mm2 | ≥ 16
4.17.38
4.17.39 | Steel structures for GIS
4.17.40 | Manufacturer | -
4.17.41 | Place of manufacture | -
4.17.42 | Applicable standard | -
4.17.43 | Material | -
4.17.44 | Factor of safety in calculation | -
4.17.45 | Galvanization thickness:
4.17.46 | - Steel sections thicker than 5 mm | μm
4.17.47 | - Steel sections 2 mm-5 mm μm | μm
4.17.48 | - Bolts and nuts μm | μm
4.17.49 | Bolts and nuts:
4.17.50 | - Securing with plain and spring washers | yes/no
4.17.51 | - yes/no
4.17.52 | - Minimum quality
4.17.53 | Tests according to relevant standards and Employer's Requirements | yes/no | yes
4.18 | Gas service cart (see 220kV GIS) | -
4.18.1 | Suitable to use for 132kV GIS | - | yes
4.19 | SF6 gas filling cart with wire-braided hoses (see 220kV GIS)
4.19.1 | Suitable to use for 132kV GIS | - | yes
4.20 | Analyzer for gas meassurement (see 220kV GIS)
4.20.1 | Suitable to use for 132kV GIS | - | yes
4.21 | Portable SF6 gas leakage detector in case (see 220kV GIS)
4.21.1 | Suitable to use for 132kV GIS | - | yes
4.22 | Density guard testing device in a case (see 220kV GIS)
4.22.1 | Suitable to use for 132kV GIS | - | yes
4.23 | Precision gauge with hose in transport case (see 220kV GIS)
4.23.1 | Suitable to use for 132kV GIS | - | yes
4.24 | Tests according to relevant standards and Employer's Requirements for SF6 service and testing equipments |  | yes
4.25 | SF6 gas
4.25.1 | Manufacturer | -
4.25.2 | Applicable standard | - | IEC 60376
4.25.3 | Amount as spare for the use of Employer | kg
4.26 | Documentation and wall boards for 132 kV GIS
4.26.1 | As specified in local language | - | yes
4.26.2 | Wall boards/charts as specified in local language | - | yes

## 5. MV Swg
Technical Data Sheets
BIDDER’S / CONTRACTOR’S GUARANTEED DATA |  | Unit | Data required | Data offered
No. | Description
5. | Medium Voltage (MV) Metal Clad Switchgear
5.1 | 33 kV Switchgear Lekhnath
5.1.1 | General Assembly
5.1.1.1 | Manufacturer | -
5.1.1.2 | Place of manufacture | -
5.1.1.3 | Model designation | -
5.1.1.4 | Applicable standard | - | IEC 62271-200
5.1.1.5 | Type | - | Metal-clad
5.1.1.6 | Insulation | - | Air-insulated
5.1.1.7 | Facility provided with pressure relief | yes/no | yes
5.1.1.8 | Location of installation | - | Indoor
5.1.1.9 | Number of phases | - | 3
5.1.1.10 | Number of busbars | - | 1
5.1.1.11 | Busbar arrangement | - | single busbar
5.1.1.12 | Expected operating lifetime | year | 30
5.1.1.13 | Loss of service continuity category | - | LSC 2B
5.1.1.14 | Switchgear partition class |  | PM
5.1.1.15 | Internal arc classification |  | IAC AFLR
25kA 1sec
5.1.1.16 | Pressure relief out of the switchgear room through a pressure relief duct |  | yes
5.1.2 | Degree of Protection
5.1.2.1 | High voltage live parts | - | IP51
5.1.2.2 | Front cover mechanism | - | IP3X
5.1.2.3 | Cable compartment | - | IP3X
5.1.2.4 | LV compartment | - | IP3X
5.1.2.5 | Overall enclosure | - | IP51
5.1.3 | Basic Electrical Data
5.1.3.1 | Nominal voltage | kV | 33
5.1.3.2 | Rated voltage Ur | kV | 36
5.1.3.3 | Rated frequency | Hz | 50
5.1.3.4 | Rated busbar current | A | 2000
5.1.3.5 | Rated short-circuit current (3 s) | kA | 25
5.1.3.6 | Rated lightning impulse withstand voltage | kVpeak | 170
5.1.3.7 | Rated power frequency short duration withstand voltage | kVrms | 70
5.1.3.8 | Power supply for drive | V DC | 220
5.1.3.9 | Power supply for auxiliary contacts | V DC | 220
5.1.3.10 | Power supply for heaters | V AC | 230
5.1.4 | Withdrawable vacuum circuit breaker unit with earthing switch
5.1.4.1 | Manufacturer | -
5.1.4.2 | Applicable standard | - | IEC 62271-100
5.1.4.3 | Dielectric medium | - | Air
5.1.4.4 | Arc distinguishing medium | - | Vacuum
5.1.4.5 | Rated current | A | 800
5.1.4.6 | Rated lightning impulse withstand voltage | kVpeak | 170
5.1.4.7 | Rated power frequency short duration withstand voltage | kVrms | 70
5.1.4.8 | Rated short-time withstand current (3 s) | kA | 25
5.1.4.9 | Rated short-circuit breaking current (CB) | kA | 25
5.1.4.10 | Rated short-circuit making current (CB) | kA | 62.5
5.1.4.11 | Rated peak withstands current | kA | 62.5
5.1.4.12 | Endurance class | -
5.1.4.13 | · breaker |  | E2, M2, C2
5.1.4.14 | · earthing switch |  | M0, E1
5.1.4.15 | Rated operating cycle | - | 0-3 min.-C0-3 min.-C0
5.1.4.16 | Drive | - | 3-pole
5.1.4.17 | Type of drive | - | Spring, motor and manual charging
5.1.5 | Direct incoming and earthing switch unit
5.1.5.1 | Manufacturer | -
5.1.5.2 | Applicable standard | - | IEC 62271-102
5.1.5.3 | Dielectric medium | - | Air
5.1.5.4 | Rated current (incoming feeder from transformer): | A | 2000
5.1.5.5 | Rated lightning impulse withstand voltage | kVpeak | 170
5.1.5.6 | Rated power frequency short duration withstand voltage | kVrms | 70
5.1.5.7 | Rated short-time withstand current (3 s) | kA | 25
5.1.5.8 | Rated peak withstands current | kA | 62.5
5.1.5.9 | Endurance class (earthing switch) | - | M0, E1
5.1.6 | Current transformer
5.1.6.1 | Manufacturer | -
5.1.6.2 | Applicable standard | - | IEC 61869-1
IEC 61869-2
5.1.6.3 | Highest voltage for equipment Um | kV | 36
5.1.6.4 | Rated lightning impulse withstand voltage | kVpeak | 170
5.1.6.5 | Rated power frequency withstand voltage | kVrms | 70
5.1.6.6 | Rated primary current incomer and earthing switch unit | - | -
5.1.6.7 | for measuring/metering/prot. | A | 150-300-600
5.1.6.8 | for busbar protection | A | N/A
5.1.6.9 | Rated primary current auxiiliary transformer feeder | - | -
5.1.6.10 | for measuring/metering/prot. | A | 150-300-600
5.1.6.11 | for busbar protection | A | N/A
5.1.6.12 | Number of cores for incomer and earthing switch unit | - | -
5.1.6.13 | for metering | - | N/A
5.1.6.14 | for protection | - | 2
5.1.6.15 | for busbar protection | - | N/A
5.1.6.16 | Number of cores for auxiliary transformer feeder | - | -
5.1.6.17 | for metering | - | 1
5.1.6.18 | for protection | - | 1
5.1.6.19 | for busbar protection | - | N/A
5.1.6.20 | Rated secondary current: | A | 1
5.1.6.21 | Accuracy class: | - | -
5.1.6.22 | for metering | - | 0.2S
5.1.6.23 | for protection | - | 5P 20
5.1.6.24 | for busbar protection | - | N/A
5.1.6.25 | Rated burden:
5.1.6.26 | for metering core | VA | 15
5.1.6.27 | for protection cores | VA | 30
5.1.6.28 | for busbar protection cores | VA | N/A
5.1.7 | Core Balance CT (CBCT)
5.1.7.1 | Manufacturer | -
5.1.7.2 | Applicable standard | - | IEC 61869-1
IEC 61869-2
5.1.7.3 | Ratio |  | 300/1
5.1.7.4 | Accuracy class: |  | 5P20
5.1.7.5 | Burden | VA | 30
5.1.8 | Voltage transformer (metering unit) | -
5.1.8.1 | Manufacturer | -
5.1.8.2 | Applicable standard | - | IEC 61869-1
IEC 61869-3
5.1.8.3 | Type |  | Inductive
5.1.8.4 | Ferro resonance damper |  | No
5.1.8.5 | Withdrawable |  | yes
5.1.8.6 | Protected by fuse |  | yes
5.1.8.7 | Highest voltage for equipment Um | kV | 36
5.1.8.8 | Rated lightning impulse withstand voltage | kVpeak | 170
5.1.8.9 | Rated power frequency withstand voltage | kVrms | 70
5.1.8.10 | Primary voltage | kV | 33 / √3
5.1.8.11 | Number of secondary windings | - | 3
5.1.8.12 | Secondary voltage | V | 0.110 / √3
|  | V | 0.110 / √3
|  | V | 0.110 / 3
5.1.8.13 | Accuracy class metering | - | 0.5
5.1.8.14 | Accuracy class protection | - | 3P
5.1.8.15 | Burden | VA | 50
5.1.9 | Lightning Arresters | -
5.1.9.1 | Manufacturer | -
5.1.9.2 | Model designation | -
5.1.9.3 | Applicable standard | - | IEC 60099-4
IEC 60099-5
5.1.9.4 | Type |  | Indoor
5.1.9.5 | System data: | kV
5.1.9.6 | · Nominal system voltage | kV | 33
5.1.9.7 | · Highest system voltage | Hz | 36
5.1.9.8 | · System frequency |  | 50
5.1.9.9 | Nominal discharge current | kA | 10 / 20 subject to calculation
5.1.9.10 | Line discharge class |  | subject to calculation
5.1.9.11 | Rated voltage Ur | kV | 27
5.1.9.12 | Maximum continuous operating voltage Uc | kV | 21
5.1.10 | Capacitive voltage indicator
5.1.10.1 | Type of capacitive voltage indicator
5.1.11 | Main Dimensions | -
5.1.11.1 | Number of individual panels | -
5.1.11.2 | Dimensions of the individual panels L x W x H | mm
5.1.11.3 | Weight of the individual panels | kg
5.1.12 | Tests
5.1.12.1 | Circuit-breaker |  | E2, M2, C2
5.1.12.2 | Earthing switch | yes/no | M0, E1
5.1.12.3 | Tests according to VII-5 Technical Specification | yes/no | yes
5.2 | 33 kV Switchgear Damauli
5.2.1 | General Assembly
5.2.1.1 | Manufacturer | -
5.2.1.2 | Place of manufacture | -
5.2.1.3 | Model designation | -
5.2.1.4 | Applicable standard | - | IEC 62271-200
5.2.1.5 | Type | - | Metal-clad
5.2.1.6 | Insulation | - | Air-insulated
5.2.1.7 | Facility provided with pressure relief | yes/no | yes
5.2.1.8 | Location of installation | - | Indoor
5.2.1.9 | Number of phases | - | 3
5.2.1.10 | Number of busbars | - | 1
5.2.1.11 | Busbar arrangement | - | single busbar
5.2.1.12 | Expected operating lifetime | year | 30
5.2.1.13 | Loss of service continuity category | - | LSC 2B
5.2.1.14 | Switchgear partition class |  | PM
5.2.1.15 | Internal arc classification |  | IAC AFLR
25kA 1sec
5.2.1.16 | Pressure relief out of the switchgear room through a pressure relief duct |  | yes
5.2.2 | Degree of Protection
5.2.2.1 | High voltage live parts | - | IP51
5.2.2.2 | Front cover mechanism | - | IP3X
5.2.2.3 | Cable compartment | - | IP3X
5.2.2.4 | LV compartment | - | IP3X
5.2.2.5 | Overall enclosure | - | IP51
5.2.3 | Basic Electrical Data
5.2.3.1 | Nominal voltage | kV | 33
5.2.3.2 | Rated voltage Ur | kV | 36
5.2.3.3 | Rated frequency | Hz | 50
5.2.3.4 | Rated busbar current | A | 2000
5.2.3.5 | Rated short-circuit current (3 s) | kA | 25
5.2.3.6 | Rated lightning impulse withstand voltage | kVpeak | 170
5.2.3.7 | Rated power frequency short duration withstand voltage | kVrms | 70
5.2.3.8 | Power supply for drive | V DC | 220
5.2.3.9 | Power supply for auxiliary contacts | V DC | 220
5.2.3.10 | Power supply for heaters | V AC | 230
5.2.4 | Withdrawable vacuum circuit breaker unit with earthing switch
5.2.4.1 | Manufacturer | -
5.2.4.2 | Applicable standard | - | IEC 62271-100
5.2.4.3 | Dielectric medium | - | Air
5.2.4.4 | Arc distinguishing medium | - | Vacuum
5.2.4.5 | Rated current incomer / buscoupler | A | 2000
5.2.4.6 | Rated current outgoing feeder | A | 800
5.2.4.7 | Rated lightning impulse withstand voltage | kVpeak | 170
5.2.4.8 | Rated power frequency short duration withstand voltage | kVrms | 70
5.2.4.9 | Rated short-time withstand current (3 s) | kA | 25
5.2.4.10 | Rated short-circuit breaking current (CB) | kA | 25
5.2.4.11 | Rated short-circuit making current (CB) | kA | 62.5
5.2.4.12 | Rated peak withstands current | kA | 62.5
5.2.4.13 | Endurance class | -
5.2.4.14 | · breaker |  | E2, M2, C2
5.2.4.15 | · earthing switch |  | M0, E1
5.2.4.16 | Rated operating cycle | - | 0-3 min.-C0-3 min.-C0
5.2.4.17 | Drive | - | 3-pole
5.2.4.18 | Type of drive | - | Spring, motor and manual charging
5.2.5 | Current transformer
5.2.5.1 | Manufacturer | -
5.2.5.2 | Applicable standard | - | IEC 61869-1
IEC 61869-2
5.2.5.3 | Highest voltage for equipment Um | kV | 36
5.2.5.4 | Rated lightning impulse withstand voltage | kVpeak | 170
5.2.5.5 | Rated power frequency withstand voltage | kVrms | 70
5.2.5.6 | Rated primary current incomer / buscoupler | - | -
5.2.5.7 | for measuring/metering/prot. | A | 600-1200
5.2.5.8 | for busbar protection | A | 1600
5.2.5.9 | Rated primary current outgoing feeder | - | -
5.2.5.10 | for measuring/metering/prot. | A | 200-400-800
5.2.5.11 | for busbar protection | A | 1600
5.2.5.12 | Number of cores for incomer | - | -
5.2.5.13 | for metering | - | 1
5.2.5.14 | for protection | - | 2
5.2.5.15 | for busbar protection | - | 1
5.2.5.16 | Number of cores for buscoupler
5.2.5.17 | for protection | - | 1
5.2.5.18 | for busbar protection | - | 1
5.2.5.19 | Number of cores for outgoing feeder | - | -
5.2.5.20 | for metering | - | 1
5.2.5.21 | for protection | - | 1
5.2.5.22 | for busbar protection | - | 1
5.2.5.23 | Rated secondary current: | A | 1
5.2.5.24 | Accuracy class: | - | -
5.2.5.25 | for metering | - | 0.5
5.2.5.26 | for protection | - | 5P 20
5.2.5.27 | for busbar protection | - | 5P 20
5.2.5.28 | Rated burden:
5.2.5.29 | for metering core | VA | 15
5.2.5.30 | for protection cores | VA | 30
5.2.5.31 | for busbar protection cores | VA | 30
5.2.6 | Core Balance CT (CBCT)
5.2.6.1 | Manufacturer | -
5.2.6.2 | Applicable standard | - | IEC 61869-1
IEC 61869-2
5.2.6.3 | Ratio |  | 300/1
5.2.6.4 | Accuracy class: |  | 5P20
5.2.6.5 | Burden | VA | 30
5.2.7 | Voltage transformer (metering unit) Damauli | -
5.2.7.1 | Manufacturer | -
5.2.7.2 | Applicable standard |  | IEC 61869-1
|  | - | IEC 61869-3
5.2.7.3 | Type |  | Inductive
5.2.7.4 | Ferro resonance damper |  | No
5.2.7.5 | Withdrawable |  | yes
5.2.7.6 | Protected by fuse |  | yes
5.2.7.7 | Highest voltage for equipment Um | kV | 36
5.2.7.8 | Rated lightning impulse withstand voltage | kVpeak | 170
5.2.7.9 | Rated power frequency withstand voltage | kVrms | 70
5.2.7.10 | Primary voltage | kV | 33 / √3
5.2.7.11 | Number of secondary windings | - | 2
5.2.7.12 | Secondary voltage | V | 0.110 / √3
|  | V | 0.110 / √3
5.2.7.13 | Accuracy class metering | - | 0,5
5.2.7.14 | Accuracy class protection | - | 3P
5.2.7.15 | Burden | VA | 50
5.2.8 | Lightning Arresters | -
5.2.8.1 | Manufacturer | -
5.2.8.3 | Model designation | -
5.2.8.4 | Applicable standard | - | IEC 60099-4
IEC 60099-5
5.2.8.5 | Type |  | Indoor
5.2.8.6 | System data: | kV
5.2.8.7 | · Nominal system voltage | kV | 33
5.2.8.8 | · Highest system voltage | Hz | 36
5.2.8.9 | · System frequency |  | 50
5.2.8.10 | Nominal discharge current | kA | 10 / 20 subject to calculation
5.2.8.11 | Line discharge class |  | subject to calculation
5.2.8.12 | Rated voltage Ur | kV | 27
5.2.8.13 | Maximum continuous operating voltage Uc | kV | 21
5.2.9 | Capacitive voltage indicator
5.2.9.1 | Type of capacitive voltage indicator
5.2.10 | Main Dimensions Damauli | -
5.2.10.1 | Number of individual panels | -
5.2.10.2 | Dimensions of the individual panels L x W x H | mm
5.2.10.3 | Weight of the individual panels | kg
5.2.11 | Tests
5.2.11.1 | Circuit-breaker |  | E2, M2, C2
5.2.11.2 | Earthing switch | yes/no | M0, E1
5.2.11.3 | Tests according to VII-5 Technical Specification | yes/no | yes
5.3 | 11 kV Switchgear Damauli
5.3.1 | General Assembly
5.3.1.1 | Manufacturer | -
5.3.1.2 | Place of manufacture | -
5.3.1.3 | Model designation | -
5.3.1.4 | Applicable standard | - | IEC 62271-200
5.3.1.5 | Type | - | Metal-clad
5.3.1.6 | Insulation | - | Air-insulated
5.3.1.7 | Facility provided with pressure relief | yes/no | yes
5.3.1.8 | Location of installation | - | Indoor
5.3.1.9 | Number of phases | - | 3
5.3.1.10 | Number of busbars | - | 1
5.3.1.11 | Busbar arrangement | - | single busbar
5.3.1.12 | Expected operating lifetime | year | 30
5.3.1.13 | Loss of service continuity category | - | LSC 2B
5.3.1.14 | Switchgear partition class |  | PM
5.3.1.15 | Internal arc classification |  | IAC AFLR
25kA 1sec
5.3.1.16 | Pressure relief out of the switchgear room through a pressure relief duct |  | yes
5.3.2 | Degree of Protection
5.3.2.1 | High voltage live parts | - | IP51
5.3.2.2 | Front cover mechanism | - | IP3X
5.3.2.3 | Cable compartment | - | IP3X
5.3.2.4 | LV compartment | - | IP3X
5.3.2.5 | Overall enclosure | - | IP51
5.3.3 | Basic Electrical Data
5.3.3.1 | Nominal voltage | kV | 11
5.3.3.2 | Rated voltage Ur | kV | 12
5.3.3.3 | Rated frequency | Hz | 50
5.3.3.4 | Rated busbar current | A | 1250
5.3.3.5 | Rated short-circuit current (3 s) | kA | 25
5.3.3.6 | Rated lightning impulse withstand voltage | kVpeak | 75
5.3.3.7 | Rated power frequency short duration withstand voltage | kVrms | 28
5.3.3.8 | Power supply for drive | V DC | 220
5.3.3.9 | Power supply for auxiliary contacts | V DC | 220
5.3.3.10 | Power supply for heaters | V AC | 230
5.3.4 | Withdrawable vacuum circuit breaker unit with earthing switch
5.3.4.1 | Manufacturer | -
5.3.4.2 | Applicable standard | - | IEC 62271-100
5.3.4.3 | Dielectric medium | - | Air
5.3.4.4 | Arc distinguishing medium | - | Vacuum
5.3.4.5 | Rated current incomer / buscoupler | A | 1250
5.3.4.6 | Rated current outgoing feeder | A | 800
5.3.4.7 | Rated lightning impulse withstand voltage | kVpeak | 75
5.3.4.8 | Rated power frequency short duration withstand voltage | kVrms | 28
5.3.4.9 | Rated short-time withstand current (3 s) | kA | 25
5.3.4.10 | Rated short-circuit breaking current (CB) | kA | 25
5.3.4.11 | Rated short-circuit making current (CB) | kA | 62.5
5.3.4.12 | Rated peak withstands current | kA | 62.5
5.3.4.13 | Endurance class | -
5.3.4.14 | · breaker |  | E2, M2, C2
5.3.4.15 | · earthing switch |  | M0, E1
5.3.4.16 | Rated operating cycle | - | 0-3 min.-C0-3 min.-C0
5.3.4.17 | Drive | - | 3-pole
5.3.4.18 | Type of drive | - | Spring, motor and manual charging
5.3.5 | Current transformer
5.3.5.1 | Manufacturer | -
5.3.5.3 | Applicable standard | - | IEC 61869-1
IEC 61869-2
5.3.5.3 | Highest voltage for equipment Um | kV | 12
5.3.5.4 | Rated lightning impulse withstand voltage | kVpeak | 75
5.3.5.5 | Rated power frequency withstand voltage | kVrms | 28
5.3.5.6 | Rated primary current incomer / buscoupler | - | -
5.3.5.7 | for measuring/metering/prot. | A | 600-900-1200/1
5.3.5.8 | for busbar protection | A | N/A
5.3.5.9 | Rated primary current outgoing feeder | - | -
5.3.5.10 | for measuring/metering/prot. | A | 200-400/1
5.3.5.11 | for busbar protection | A | N/A
5.3.5.12 | Number of cores for incomer | - | -
5.3.5.13 | for metering | - | 1
5.3.5.14 | for protection | - | 2
5.3.5.15 | Number of cores for buscoupler
5.3.5.16 | for protection | - | 1
5.3.5.17 | Number of cores for outgoing feeder | - | -
5.3.5.18 | for metering | - | 1
5.3.5.19 | for protection | - | 1
5.3.5.30 | Rated secondary current: | - | -
5.3.5.31 | for metering | A | 1
5.3.5.32 | for protection | A | 1
5.3.5.33 | Accuracy class: | - | -
5.3.5.34 | for metering | - | 0.5
5.3.5.35 | for protection | - | 5P 20
5.3.5.36 | Rated burden:
5.3.5.37 | for metering core | VA | 15
5.3.5.38 | for protection cores | VA | 30
5.3.6 | Core Balance CT (CBCT)
5.3.6.1 | Manufacturer | -
5.3.6.2 | Applicable standard | - | IEC 61869-1
IEC 61869-2
5.3.6.3 | Ratio |  | 300/1
5.3.6.4 | Accuracy class: |  | 5P20
5.3.6.5 | Burden | VA | 30
5.3.7 | Voltage transformer (metering unit) | -
5.3.7.1 | Manufacturer | -
5.3.7.2 | Applicable standard |  | IEC 61869-1
|  | - | IEC 61869-3
5.3.7.3 | Type |  | Inductive
5.3.7.4 | Ferro resonance damper |  | yes
5.3.7.5 | Withdrawable |  | yes
5.3.7.6 | Protected by fuse |  | yes
5.3.7.7 | Highest voltage for equipment Um | kV | 12
5.3.7.8 | Rated lightning impulse withstand voltage | kVpeak | 75
5.3.7.9 | Rated power frequency withstand voltage | kVrms | 28
5.3.7.10 | Primary voltage | kV | 11 / √3
5.3.7.11 | Number of secondary windings | - | 2
5.3.7.12 | Secondary voltage | V | 0.110 / √3
|  | V | 0.110 / √3
5.3.7.13 | Accuracy class metering | - | 0.5
5.3.7.14 | Accuracy class protection | - | 3P
5.3.7.15 | Burden | VA | 50
5.3.8 | Lightning Arresters | -
5.3.8.1 | Manufacturer | -
5.3.8.2 | Place of manufacture | -
5.3.8.3 | Model designation | -
5.3.8.4 | Applicable standard |  | IEC 60099-4
|  | - | IEC 60099-5
5.3.8.5 | Type |  | Indoor
5.3.8.6 | System data: | kV
5.3.8.7 | · Nominal system voltage | kV | 11
5.3.8.8 | · Highest system voltage | Hz | 12
5.3.8.9 | · System frequency |  | 50
5.3.8.10 | Nominal discharge current | kA | 10 / 20 subject to calculation
5.3.8.11 | Line discharge class |  | subject to calculation
5.3.8.12 | Rated voltage Ur | kV | 9
5.3.8.13 | Maximum continuous operating voltage Uc | kV | 7.2
5.3.9 | Capacitive voltage indicator
5.3.9.1 | Type of capacitive voltage indicator
5.3.10 | Main Dimensions | -
5.3.10.1 | Number of individual panels | -
5.3.10.2 | Dimensions of the individual panels L x W x H | mm
5.3.10.3 | Weight of the individual panels | kg
5.3.11 | Tests
5.3.11.1 | Circuit-breaker |  | E2, M2, C2
5.3.11.2 | Earthing switch | yes/no | M0, E1
5.3.11.3 | Tests according to VII-5 Technical Specification | yes/no | yes

## 6. Transformers
Technical Data Sheets
BIDDER’S / CONTRACTOR’S GUARANTEED DATA |  | Unit | Data required | Data offered
No. | Description
6. | Transformers
6.1 | Power Transformers and Autotransformers
6.1.1 | Autotransformer 220/132/33 kV for Lekhnath
6.1.1.1 | General Data
6.1.1.1.1 | Manufacturer | -
6.1.1.1.2 | Place of manufacture | -
6.1.1.1.3 | Applicable standard | - | IEC 60076 etc., as per VII-5 Technical Specifications
6.1.1.1.4 | 6 Sigma Quality Certification for Transformer Manufacturing Facilities | Yes/no | Yes
6.1.1.1.5 | Painting as per ISO 12944 C5-M | Yes/no | Yes
6.1.1.1.6 | Service altitude | m | <1000
6.1.1.1.7 | Ambient temperature (max.) | °C | 40
6.1.1.1.8 | Type | - | Autotransformer Single-Phase
6.1.1.1.9 | Rated voltage | kV | 220/√3 / 132/√3 / 33
6.1.1.1.10 | Vector group single phase transformer | - | Ia0i0
6.1.1.1.11 | Vector group three phase bank | - | YNa0d11
6.1.1.1.12 | Type of Cooling |  | ONAN/ONAF
6.1.1.1.13 | Type of insulation: | - | -
6.1.1.1.14 | · primary | - | Graded
6.1.1.1.15 | · secondary |  | Graded
6.1.1.1.16 | · tertiary | - | Uniform
6.1.1.1.17 | Location of use | - | outdoor
6.1.1.1.18 | Tank type | - | Upper flange
6.1.1.1.19 | Max noise level (LPA) - according to IEC 60076-10 - at a measuring distance of 2m with all forced cooling in operation | dB (A) | 70
6.1.1.1.20 | Rated frequency | Hz | 50
6.1.1.2 | Characteristics of magnetic circuit
6.1.1.2.1 | Type | - | Core type
6.1.1.2.2 | Material | - | Cold rolled grain silicon steel
6.1.1.2.3 | Maximum flux density at rated voltage and frequency | T | ≤1,65
6.1.1.3 | Temperature rise
6.1.1.3.1 | Top oil | K | 60
6.1.1.3.2 | Average winding | K | 65
6.1.1.3.3 | Hot spot winding | K | 78
6.1.1.4 | Rated power
6.1.1.4.1 | 220 kV level:
6.1.1.4.2 | · ONAN | MVA | 80
6.1.1.4.3 | · ONAF | MVA | 105
6.1.1.4.4 | 132 kV level:
6.1.1.4.5 | · ONAN | MVA | 80
6.1.1.4.6 | · ONAF | MVA | 105
6.1.1.4.7 | 33kV level:
6.1.1.4.8 | · ONAN | MVA | 25
6.1.1.4.9 | · ONAF | MVA | 33
6.1.1.5 | Rated withstand voltages for transformer windings
6.1.1.5.1 | 220 kV winding (Um=245 kV):
6.1.1.5.2 | · Rated lightning impulse withstand voltage | kVpeak | 1050
6.1.1.5.3 | · Rated short-duration induced or separate source AC withstand voltage | kVrms | 460
6.1.1.5.4 | 132 kV winding (Um=145kV):
6.1.1.5.5 | · Rated lightning impulse withstand voltage | kVpeak | 650
6.1.1.5.6 | · Rated short-duration induced or separate source AC withstand voltage | kVrms | 275
6.1.1.5.7 | 33 kV winding (Um=36 kV):
6.1.1.5.8 | · Rated lightning impulse withstand voltage | kVpeak | 250
6.1.1.5.9 | · Rated short-duration induced or separate source AC withstand voltage | kVrms | 95
6.1.1.5.10 | Neutral (Um=52 kV):
6.1.1.5.11 | · Rated lightning impulse withstand voltage | kVpeak | 250
6.1.1.5.12 | · Rated short-duration induced or separate source AC withstand voltage | kVrms | 95
6.1.1.6 | Short circuit level (3 s) of the system
6.1.1.6.1 | · 220 kV level | kA | 40
6.1.1.6.2 | · 132 kV level | kA | 31,5
6.1.1.6.3 | · 33 kV level | kA | N/A
6.1.1.7 | Impedance voltage in % at 75°C winding temperature on middle tap position at full loading, ONAF
6.1.1.7.1 | · 220 to 132 kV | % | 13
6.1.1.7.2 | · 132 to 33 kV | % | 20
6.1.1.7.3 | · 220 to 33 kV | % | 32
6.1.1.8 | Oil characteristics
6.1.1.8.1 | Mineral oil standard | - | IEC 60296
6.1.1.8.2 | Corrosive Sulphur test |  | IEC 62535
ASTM D 1275 method B
6.1.1.8.3 | Dryness of the oil after on-site installation |  | Water Content ≤5ppm
6.1.1.8.4 | Inhibited | Yes / No
6.1.1.8.5 | Manufacturer | -
6.1.1.8.6 | Oil type | inhibited/
6.1.1.8.7 | Type designation | -
6.1.1.8.8 | Minimum flash point | °C | 140
6.1.1.8.9 | Viscosity at 80°C | mm²/s
6.1.1.8.10 | Max. dielectric strength (1min.) | kV
6.1.1.8.11 | Total oil required | l
6.1.1.8.12 | Tests according to VII-5 Technical Specifications | yes/no | yes
6.1.1.9 | Bushings
6.1.1.9.1 | Applicable standard | - | IEC 60137
6.1.1.10 | 220 kV bushing | -
6.1.1.10.1 | · Manufacturer
6.1.1.10.2 | · Place of manufacture | -
6.1.1.10.3 | Type of bushing | - | RIP or RIS
6.1.1.10.4 | Type of bushing insulator | - | silicon
6.1.1.10.5 | Type designation | -
6.1.1.10.6 | Highest rated voltage | kV | 245
6.1.1.10.7 | Rated current | A | 1000
6.1.1.10.8 | Rated thermal short time current (3 s) | kA | 40
6.1.1.10.9 | Rated dynamic current | kA | 100
6.1.1.10.10 | Minimum Unified Specific Creepage Distance (USCD) | mm/kV | 43.3
6.1.1.10.11 | Rated lightning impulse withstand voltage | kVpeak | 1050
6.1.1.10.12 | Rated switching impulse withstand voltage | kVpeak | 850
6.1.1.10.13 | Power frequency withstand voltage (dry) | kVrms | 460
6.1.1.11 | 132 kV bushing | -
6.1.1.11.1 | · Manufacturer
6.1.1.11.2 | · Place of manufacture | -
6.1.1.11.3 | Type of bushing | - | RIP or RIS
6.1.1.11.4 | Type of bushing insulator | - | silicon
6.1.1.11.5 | Type designation | -
6.1.1.11.6 | Highest rated voltage | kV | 145
6.1.1.11.7 | Rated current | A | 2000
6.1.1.11.8 | Rated thermal short time current (3 s) | kA | 40
6.1.1.11.9 | Rated dynamic current | kA | 100
6.1.1.11.10 | Minimum Unified Specific Creepage Distance (USCD) | mm/kV | 43.3
6.1.1.11.11 | Rated lightning impulse withstand voltage | kVpeak | 650
6.1.1.11.12 | Power frequency withstand voltage (dry) | kVrms | 275
6.1.1.12 | 33 kV bushing
6.1.1.12.1 | · Manufacturer | -
6.1.1.12.2 | · Place of manufacture | -
6.1.1.12.3 | Type of bushing insulator | - | porcelain
6.1.1.12.4 | Type designation | -
6.1.1.12.5 | Highest rated voltage | kV | 36
6.1.1.12.6 | Rated current | A | 2500
6.1.1.12.7 | Rated thermal short time current (3 s) | kA | 50
6.1.1.12.8 | Rated dynamic current | kA | 125
6.1.1.12.9 | Minimum Unified Specific Creepage Distance (USCD) | mm/kV | 43.3
6.1.1.12.10 | Rated lightning impulse withstand voltage | kVpeak | 250
6.1.1.12.11 | Power frequency withstand voltage (dry) | kVrms | 95
6.1.1.12.12 | Minimum cantilever withstand load | N | 500
6.1.1.13 | Neutral bushing | -
6.1.1.13.1 | Manufacturer
6.1.1.13.2 | Place of manufacture | -
6.1.1.13.3 | Type of bushing | - | RIP or RIS
6.1.1.13.4 | Type of bushing insulator | - | silicon
6.1.1.13.5 | Type designation | -
6.1.1.13.6 | Highest rated voltage | kV | 52
6.1.1.13.7 | Rated current | A | 1000
6.1.1.13.8 | Rated thermal short time current (3 s) | kA | 40
6.1.1.13.9 | Rated dynamic current | kA | 100
6.1.1.13.10 | Minimum Unified Specific Creepage Distance (USCD) | mm/kV | 43.3
6.1.1.13.11 | Rated lightning impulse withstand voltage | kVpeak | 250
6.1.1.13.12 | Power frequency withstand voltage (dry) | kVrms | 95
6.1.1.13.13 | Minimum cantilever withstand load | N | 500
6.1.1.14 | Bushing current transformers
6.1.1.14.1 | 220 kV:
6.1.1.14.2 | · Ratio | A | 500-750-1250/1
6.1.1.14.3 | · Core 1 burden and accuracy | - | 5P20 30 VA
6.1.1.14.4 | · Core 2 burden and accuracy | - | 5P20 30 VA
6.1.1.14.5 | · Core 3 burden and accuracy | - | N/A
6.1.1.14.6 | 132 kV:
6.1.1.14.7 | · Ratio | A | 1250/1500/2000/1
6.1.1.14.8 | · Core 1 burden and accuracy | - | 5P20 30 VA
6.1.1.14.9 | · Core 2 burden and accuracy | - | 5P20 30 VA
6.1.1.14.10 | · Core 3 burden and accuracy | - | N/A
6.1.1.14.11 | 33 kV (both bushings):
6.1.1.14.12 | · Ratio | A | 300-600/1
6.1.1.14.13 | · Core 1 burden and accuracy | - | 5P20 30 VA
6.1.1.14.14 | · Core 2 burden and accuracy | - | 5P20 30 VA
6.1.1.14.15 | · Core 3 burden and accuracy | - | N/A
6.1.1.14.16 | Neutral:
6.1.1.14.17 | · Ratio | A | 500-750-1250/1
6.1.1.14.18 | · Core 1 burden and accuracy | - | 5P20 30 VA
6.1.1.14.19 | · Core 2 burden and accuracy | - | 5P20 30 VA
6.1.1.15 | Cooling system
6.1.1.15.1 | Type of cooling | - | ONAN/ONAF
6.1.1.15.2 | Number of coolers | pcs
6.1.1.15.3 | Cooling operation | - | Auto/Manual
6.1.1.15.4 | Control voltage for cooling and heating | V AC | 230
6.1.1.15.5 | Supply voltage of protective devices | V DC | 220
6.1.1.15.6 | Supply voltage of fans and pumps | V AC | 230/400
6.1.1.15.7 | Power demand of fans | kW
6.1.1.15.8 | Power demand of oil pumps | kW
6.1.1.16 | No load current
6.1.1.16.1 | No load current | %
6.1.1.16.2 | Magnetic flux density at rated voltage and frequency | Tesla | Max 1,65
6.1.1.16.3 | Core losses | W/kg | Max 1,05
6.1.1.17 | Losses
6.1.1.17.1 | No load losses at nominal voltage position | kW
6.1.1.17.2 | No load losses at lowest tap position | kW
6.1.1.17.3 | No load losses at highest tap position | kW
6.1.1.17.4 | Load losses at nominal tap at ONAN:
6.1.1.17.5 | Primary/Secondary | kW
6.1.1.17.6 | Primary/Tertiary | kW
6.1.1.17.7 | Secondary/Tertiary | kW
6.1.1.17.8 | Load losses at nominal tap at ONAF:
6.1.1.17.9 | Primary/Secondary | kW
6.1.1.17.10 | Primary/Tertiary | kW
6.1.1.17.11 | Secondary/Tertiary | kW
6.1.1.18 | OLTC (On-load tap-changer)
6.1.1.18.1 | Manufacturer | - | MR Germany or ABB Sweden, or equivalent
6.1.1.18.2 | Type designation | -
6.1.1.18.3 | Applicable standard | - | IEC 60214-1
6.1.1.18.4 | Type | - | vacuum
6.1.1.18.5 | Type of connection | - | line-end (constant flux)
6.1.1.18.6 | Tapping on 220kV side | % | +8 x 1,25 / -8 x 1,25
6.1.1.18.7 | Rated through current | A | -
6.1.1.18.8 | Rated short-time current:
6.1.1.18.9 | maximum (peak) | kA | -
6.1.1.18.10 | 3 seconds | kA | -
6.1.1.18.11 | Rated power frequency withstand voltage | kVrms | 275
6.1.1.18.12 | Rated lightning impulse withstand voltage | kVpeak | 650
6.1.1.18.13 | Rated operations duty (min.) | - | 600,000
6.1.1.19 | Automatic Voltage Regulation
6.1.1.19.1 | Manufacturer | -
6.1.1.19.2 | Type / designation
6.1.1.19.3 | Sensitivity | -%,+% | 0,4 to 6% of transformer voltage
6.1.1.19.4 | Response time | s | 0-15 sec to 4 min. referred to 1% deviation from desired value
6.1.1.19.5 | Range of set point adjustment | % of Un | 90 to 115% UN
6.1.1.19.6 | Current-responsive rising | % of Un | 0 to 16% UN
6.1.1.19.7 | Limitation of current effect | % of Un | 0 to 16% UN
6.1.1.19.8 | Overvoltage Umax | % of Un | 100 to 135% UN
6.1.1.19.9 | Under voltage Umin. | % of Un | 50 to 100% UN
6.1.1.19.10 | Under/Overcurrent Imin/max | x In | 60 to 120 IN
6.1.1.19.11 | Line drop compensation |  | Yes
6.1.1.19.12 | Parallel operation with other transformer | - | Yes
6.1.1.20 | Neutral Treatment
6.1.1.20.1 | Brought up to bushings and grounded | yes/no | yes
6.1.1.20.2 | Neutral surge arrester | yes/no | no
6.1.1.20.3 | Neutral disconnector | yes/no | no
6.1.1.20.4 | Neutral current transformer | yes/no | yes
6.1.1.20.5 | Solidly grounded | yes/no | yes
6.1.1.21 | Accessories
6.1.1.21.1 | Accessories according to VII-5 Technical Specification | yes/no | yes
6.1.1.21.2 | Online transformer condition monitoring system according to VII-5 Technical Specification | yes/no | yes
6.1.1.22 | Marshalling kiosks
6.1.1.22.1 | Degree of protection | - | IP55
6.1.1.22.2 | Marshalling kiosks according to VII-5 Technical Specification | yes/no | yes
6.1.1.23 | Tank mounted Surge Arrestors
6.1.1.23.1 | 220 kV Surge Arrester and Discharge Counter
6.1.1.23.1.1 | Manufacturer | - | -
6.1.1.23.1.2 | Place of manufacture | - | -
6.1.1.23.1.3 | Model designation | - | -
6.1.1.23.1.4 | Applicable standard | - | IEC 60071-1
IEC 60071-2
IEC 60099-4
IEC 60099-5
IEC 60529
IEC 60815
6.1.1.23.1.5 | Type | - | Outdoor, silicon-housed
6.1.1.23.1.6 | System data:
6.1.1.23.1.7 | · Nominal system voltage | kV | 220
6.1.1.23.1.8 | · Highest system voltage | kV | 245
6.1.1.23.1.9 | · System frequency | Hz | 50
6.1.1.23.1.10 | Rated voltage Ur | kV | 180
6.1.1.23.1.11 | Maximum continuous operating voltage Uc | kV | 144
6.1.1.23.1.12 | Rated discharge current | kA | 10 / 20 subject to calculation
6.1.1.23.1.13 | Thermal energy rating | kJ/kV | 10
6.1.1.23.1.14 | Separate earthing rod per SA, 150 mm2 | yes/no | yes
6.1.1.23.1.15 | Discharge Counter:
6.1.1.23.1.16 | Manufacturer | -
6.1.1.23.1.17 | Model designation | -
6.1.1.23.1.18 | Display | -
6.1.1.23.1.19 | Number of impulses | yes/no | yes
6.1.1.23.1.20 | Leakage current measurement, total current | yes/no | yes
6.1.1.23.1.21 | Protection class | - | IP55 W
6.1.1.23.1.22 | Number of counters per three (3) 1-ph arresters | - | 3
6.1.1.23.2 | 132 kV Surge Arrester and Discharge Counter
6.1.1.23.2.1 | Manufacturer | - | -
6.1.1.23.2.2 | Place of manufacture | - | -
6.1.1.23.2.3 | Model designation | - | -
6.1.1.23.2.4 | Applicable standard | - | IEC 60071-1
IEC 60071-2
IEC 60099-4
IEC 60099-5
IEC 60529
IEC 60815
6.1.1.23.2.5 | Type | - | Outdoor, silicon-housed
6.1.1.23.2.6 | System data:
6.1.1.23.2.7 | · Nominal system voltage | kV | 132
6.1.1.23.2.8 | · Highest system voltage | kV | 145
6.1.1.23.2.9 | · System frequency | Hz | 50
6.1.1.23.2.10 | Rated voltage Ur | kV | 108
6.1.1.23.2.11 | Maximum continuous operating voltage Uc | kV | 86
6.1.1.23.2.12 | Rated discharge current | kA | 10 / 20 subject to calculation
6.1.1.23.2.13 | Thermal energy rating | kJ/kV | 10
6.1.1.23.2.14 | Separate earthing rod per SA, 150 mm2 | yes/no | yes
6.1.1.23.2.15 | Discharge Counter:
6.1.1.23.2.16 | Manufacturer | -
6.1.1.23.2.17 | Model designation | -
6.1.1.23.2.18 | Display | -
6.1.1.23.2.19 | Number of impulses | yes/no | yes
6.1.1.23.2.20 | Leakage current measurement, total current | yes/no | yes
6.1.1.23.2.21 | Protection class | - | IP 55 W
6.1.1.23.2.22 | Number of counters per three (3) 1-ph arresters | - | 3
6.1.1.23.3 | 33 kV Surge Arrester
6.1.1.23.3.1 | Manufacturer | - | -
6.1.1.23.3.2 | Place of manufacture | - | -
6.1.1.23.3.3 | Model designation | - | -
6.1.1.23.3.4 | Applicable standard | - | IEC 60071-1
IEC 60071-2
IEC 60099-4
IEC 60099-5
IEC 60529
IEC 60815
6.1.1.23.3.5 | Type | - | Outdoor, silicon-housed
6.1.1.23.3.6 | System data:
6.1.1.23.3.7 | · Nominal system voltage | kV | 33
6.1.1.23.3.8 | · Highest system voltage | kV | 36
6.1.1.23.3.9 | · System frequency | Hz | 50
6.1.1.23.3.10 | Rated voltage Ur | kV | 27
6.1.1.23.3.11 | Maximum continuous operating voltage Uc | kV | 21
6.1.1.23.3.12 | Rated discharge current | kA | 10 / 20 subject to calculation
6.1.1.23.3.13 | Thermal energy rating | kJ/kV | 10
6.1.1.24 | Transformer Main dimensions
6.1.1.24.1 | Total length x width x height | m | -
6.1.1.24.2 | Tank length x width x height | m | -
6.1.1.24.3 | Gross weight | kg | -
6.1.1.24.4 | Transport weight | kg | -
6.1.1.24.5 | Volume of oil | m3 | -
6.1.1.24.6 | Weight of oil | kg | -
6.1.1.24.7 | Max. admitted accelerations in XYZ-directions during transport | g | -
6.1.1.25 | Tests
6.1.1.25.1 | Tests according to VII-5 Technical Specification | yes/no | yes
6.1.2 | Power Transformer 220/132 kV for Damauli
6.1.2.1 | General Data
6.1.2.1.1 | Manufacturer | -
6.1.2.1.2 | Place of manufacture | -
6.1.2.1.3 | Applicable standard | - | IEC 60076 etc., as per VII-5 Technical Specifications
6.1.2.1.4 | 6 Sigma Quality Certification for Transformer Manufacturing Facilities | Yes/no | Yes
6.1.2.1.5 | Painting as per ISO 12944 C5-M | Yes/no | Yes
6.1.2.1.6 | Service altitude | m | <1000
6.1.2.1.7 | Ambient temperature (max.) | °C | 50
6.1.2.1.8 | Type | - | Power Transformer three-Phase
6.1.2.1.9 | Rated voltage | kV | 220 / 132
6.1.2.1.10 | Vector group | - | YNyn0+d
6.1.2.1.11 | Type of Cooling |  | ONAN/ONAF
6.1.2.1.12 | Type of insulation: | - | -
6.1.2.1.13 | · primary | - | Uniform
6.1.2.1.14 | · secondary |  | Uniform
6.1.2.1.15 | · tertiary | - | Uniform
6.1.2.1.16 | Location of use | - | outdoor
6.1.2.1.17 | Tank type | - | Upper flange
6.1.2.1.18 | Max noise level (LPA) - according to IEC 60076-10 - at a measuring distance of 2m with all forced cooling in operation | dB (A) | 70
6.1.2.1.19 | Rated frequency | Hz | 50
6.1.2.2 | Characteristics of magnetic circuit
6.1.2.2.1 | Type | - | Core type
6.1.2.2.2 | Material | - | Cold rolled grain silicon steel
6.1.2.2.3 | Maximum flux density at rated voltage and frequency | T | ≤1,65
6.1.2.3 | Temperature rise
6.1.2.3.1 | Top oil | K | 50
6.1.2.3.2 | Average winding | K | 55
6.1.2.3.3 | Hot spot winding | K | 68
6.1.2.4 | Rated power
6.1.2.4.1 | · ONAN | MVA | 50
6.1.2.4.2 | · ONAF | MVA | 63
6.1.2.5 | Rated withstand voltages for transformer windings
6.1.2.5.1 | 220 kV winding (Um=245 kV):
6.1.2.5.2 | · Rated lightning impulse withstand voltage | kVpeak | 1050
6.1.2.5.3 | · Rated short-duration induced or separate source AC withstand voltage | kVrms | 460
6.1.2.5.4 | 132 kV winding (Um=123 kV):
6.1.2.5.5 | · Rated lightning impulse withstand voltage | kVpeak | 650
6.1.2.5.6 | · Rated short-duration induced or separate source AC withstand voltage | kVrms | 275
6.1.2.5.7 | Neutral (Um=52 kV):
6.1.2.5.8 | · Rated lightning impulse withstand voltage | kVpeak | N/A
6.1.2.5.9 | · Rated short-duration induced or separate source AC withstand voltage | kVrms | N/A
6.1.2.6 | Short circuit level (3 s) of the system
6.1.2.6.1 | · 220 kV level | kA | 40
6.1.2.6.2 | · 132 kV level | kA | 40
6.1.2.7 | Impedance voltage in % at 75°C winding temperature on middle tap position at full loading, ONAF | % | 12
6.1.2.8 | Oil characteristics
6.1.2.8.1 | Mineral oil standard | - | IEC 60296
6.1.2.8.2 | Corrosive Sulphur test |  | IEC 62535
ASTM D 1275 method B
6.1.2.8.3 | Dryness of the oil after on-site installation |  | Water Content ≤5ppm
6.1.2.8.4 | Inhibited | Yes / No
6.1.2.8.5 | Manufacturer | -
6.1.2.8.6 | Oil type | inhibited/
6.1.2.8.7 | Type designation | -
6.1.2.8.8 | Minimum flash point | °C | 140
6.1.2.8.9 | Viscosity at 80°C | mm²/s
6.1.2.8.10 | Max. dielectric strength (1min.) | kV
6.1.2.8.11 | Total oil required | l
6.1.2.8.12 | Tests according to VII-5 Technical Specifications | yes/no | yes
6.1.2.9 | Bushings
6.1.2.9.1 | Applicable standard | - | IEC 60137
6.1.2.10 | 220 kV bushing | -
6.1.2.10.1 | · Manufacturer
6.1.2.10.2 | · Place of manufacture | -
6.1.2.10.3 | Type of bushing | - | RIP or RIS
6.1.2.10.4 | Type of bushing insulator | - | silicon
6.1.2.10.5 | Type designation | -
6.1.2.10.6 | Highest rated voltage | kV | 245
6.1.2.10.7 | Rated current | A | 800
6.1.2.10.8 | Rated thermal short time current (3 s) | kA | 40
6.1.2.10.9 | Rated dynamic current | kA | 100
6.1.2.10.10 | Minimum Unified Specific Creepage Distance (USCD) | mm/kV | 43.3
6.1.2.10.11 | Rated lightning impulse withstand voltage | kVpeak | 1050
6.1.2.10.12 | Rated switching impulse withstand voltage | kVpeak | 850
6.1.2.10.13 | Power frequency withstand voltage (dry) | kVrms | 460
6.1.2.11 | 132 kV bushing | -
6.1.2.11.1 | · Manufacturer
6.1.2.11.2 | · Place of manufacture | -
6.1.2.11.3 | Type designation | -
6.1.2.11.4 | Type of bushing | - | RIP or RIS
6.1.2.11.5 | Type of bushing insulator | - | silicon
6.1.2.11.6 | Highest rated voltage | kV | 145
6.1.2.11.7 | Rated current | A | 800
6.1.2.11.8 | Rated thermal short time current (3 s) | kA | 40
6.1.2.11.9 | Rated dynamic current | kA | 100
6.1.2.11.10 | Minimum Unified Specific Creepage Distance (USCD) | mm/kV | 43.3
6.1.2.11.11 | Rated lightning impulse withstand voltage | kVpeak | 650
6.1.2.11.12 | Power frequency withstand voltage (dry) | kVrms | 275
6.1.2.13 | Neutral bushings | -
6.1.2.13.1 | Manufacturer
6.1.2.13.2 | Place of manufacture | -
6.1.2.13.3 | Type of bushing | - | RIP or RIS
6.1.2.13.4 | Type of bushing insulator | - | silicon
6.1.2.13.5 | Type designation | -
6.1.2.13.6 | Highest rated voltage | kV | 52
6.1.2.13.7 | Rated current | A | 800
6.1.2.13.8 | Rated thermal short time current (3 s) | kA | 40
6.1.2.13.9 | Rated dynamic current | kA | 100
6.1.2.13.10 | Minimum Unified Specific Creepage Distance (USCD) | mm/kV | 43.3
6.1.2.13.11 | Rated lightning impulse withstand voltage | kVpeak | 250
6.1.2.13.12 | Power frequency withstand voltage (dry) | kVrms | 95
6.1.2.13.13 | Minimum cantilever withstand load | N | 500
6.1.2.14 | Bushing current transformers
6.1.2.14.1 | 220 kV:
6.1.2.14.2 | · Ratio | A | 200/400/600/1
6.1.2.14.3 | · Core 1 burden and accuracy | - | 5P20 30 VA
6.1.2.14.4 | · Core 2 burden and accuracy | - | 5P20 30 VA
6.1.2.14.5 | · Core 3 burden and accuracy | - | N/A
6.1.2.14.6 | 132 kV:
6.1.2.14.7 | · Ratio | A | 400/600/800/1
6.1.2.14.8 | · Core 1 burden and accuracy | - | 5P20 30 VA
6.1.2.14.9 | · Core 2 burden and accuracy | - | 5P20 30 VA
6.1.2.14.10 | · Core 3 burden and accuracy | - | N/A
6.1.2.14.11 | Neutral 220 kV side:
6.1.2.14.12 | · Ratio | A | 200/400/600/1
6.1.2.14.13 | · Core 1 burden and accuracy | - | 5P20 30 VA
6.1.2.14.14 | · Core 2 burden and accuracy | - | 5P20 30 VA
6.1.2.14.15 | Neutral 132 kV side:
6.1.2.14.16 | · Ratio | A | 400/600/800/1
6.1.2.14.17 | · Core 1 burden and accuracy | - | 5P20 30 VA
6.1.2.14.18 | · Core 2 burden and accuracy | - | 5P20 30 VA
6.1.2.15 | Cooling system
6.1.2.15.1 | Type of cooling | - | ONAN/ONAF
6.1.2.15.2 | Number of coolers | pcs
6.1.2.15.3 | Cooling operation | - | Auto/Manual
6.1.2.15.4 | Control voltage for cooling and heating | V AC | 230
6.1.2.15.5 | Supply voltage of protective devices | V DC | 220
6.1.2.15.6 | Supply voltage of fans and pumps | V AC | 230/400
6.1.2.15.7 | Power demand of fans | kW
6.1.2.15.8 | Power demand of oil pumps | kW
6.1.2.16 | No load current
6.1.2.16.1 | No load current | %
6.1.2.16.2 | Magnetic flux density at rated voltage and frequency | Tesla | Max 1,65
6.1.2.16.3 | Core losses | W/kg | Max 1,05
6.1.2.17 | Losses
6.1.2.17.1 | No load losses at nominal voltage position | kW
6.1.2.17.2 | No load losses at lowest tap position | kW
6.1.2.17.3 | No load losses at highest tap position | kW
6.1.2.17.4 | Load losses at nominal tap at ONAN: | kW
6.1.2.17.5 | Load losses at nominal tap at ONAF: | kW
6.1.2.18 | OLTC (On-load tap-changer)
6.1.2.18.1 | Manufacturer | - | MR Germany or ABB Sweden, or equivalent
6.1.2.18.2 | Type designation | -
6.1.2.18.3 | Applicable standard | - | IEC 60214-1
6.1.2.18.4 | Type | - | vacuum
6.1.2.18.5 | Tapping on 220kV side | % | +8 x 1,25 / - 8 x 1,25
6.1.2.18.6 | Rated through current | A | -
6.1.2.18.7 | Rated short-time current:
6.1.2.18.8 | maximum (peak) | kA | -
6.1.2.18.9 | 3 seconds | kA | -
6.1.2.18.10 | Rated power frequency withstand voltage | kVrms | -
6.1.2.18.11 | Rated lightning impulse withstand voltage | kVpeak | -
6.1.2.18.12 | Rated operations duty (min.) | - | 600 000
6.1.2.19 | Automatic Voltage Regulation
6.1.2.19.1 | Manufacturer | -
6.1.2.19.2 | Type / designation
6.1.2.19.3 | Sensitivity | -%,+% | 0,4 to 6% of transformer voltage
6.1.2.19.4 | Response time | s | 0-15 sec to 4 min. referred to 1% deviation from desired value
6.1.2.19.5 | Range of set point adjustment | % of Un | 90 to 115% UN
6.1.2.19.6 | Current-responsive rising | % of Un | 0 to 16% UN
6.1.2.19.7 | Limitation of current effect | % of Un | 0 to 16% UN
6.1.2.19.8 | Overvoltage Umax | % of Un | 100 to 135% UN
6.1.2.19.9 | Under voltage Umin. | % of Un | 50 to 100% UN
6.1.2.19.10 | Under/Overcurrent Imin/max | x In | 60 to 120 IN
6.1.2.19.11 | Line drop compensation |  | Yes
6.1.2.19.12 | Parallel operation with other transformer | - | Yes
6.1.2.20 | Neutral Treatment
6.1.2.20.1 | Brought up to bushings and grounded | yes/no | yes
6.1.2.20.2 | Neutral surge arrester | yes/no | no
6.1.2.20.3 | Neutral disconnector | yes/no | no
6.1.2.20.4 | Neutral current transformer | yes/no | yes
6.1.2.20.5 | Solidly grounded | yes/no | yes
6.1.2.21 | Accessories
6.1.2.21.1 | Accessories according to VII-5 Technical Specification | yes/no | yes
6.1.2.21.2 | Online transformer condition monitoring system according to VII-5 Technical Specification | yes/no | no
6.1.2.22 | Marshalling kiosks
6.1.2.22.1 | Degree of protection | - | IP55
6.1.2.22.2 | Marshalling kiosks according to VII-5 Technical Specification | yes/no | yes
6.1.2.23 | Tank mounted Surge Arrestors
6.1.2.23.1 | 220 kV Surge Arrester and Discharge Counter
6.1.2.23.1.1 | Manufacturer | - | -
6.1.2.23.1.2 | Place of manufacture | - | -
6.1.2.23.1.3 | Model designation | - | -
6.1.2.23.1.4 | Applicable standard | - | IEC 60071-1
IEC 60071-2
IEC 60099-4
IEC 60099-5
IEC 60529
IEC 60815
6.1.2.23.1.5 | Type | - | Outdoor, silicon-housed
6.1.2.23.1.6 | System data:
6.1.2.23.1.7 | · Nominal system voltage | kV | 220
6.1.2.23.1.8 | · Highest system voltage | kV | 245
6.1.2.23.1.9 | · System frequency | Hz | 50
6.1.2.23.1.10 | Rated voltage Ur | kV | 180
6.1.2.23.1.11 | Maximum continuous operating voltage Uc | kV | 144
6.1.2.23.1.12 | Rated discharge current | kA | 10 / 20 subject to calculation
6.1.2.23.1.13 | Thermal energy rating | kJ/kV | 10
6.1.2.23.1.14 | Separate earthing rod per SA, 150 mm2 | yes/no | yes
6.1.2.23.1.15 | Discharge Counter:
6.1.2.23.1.16 | Manufacturer | -
6.1.2.23.1.17 | Model designation | -
6.1.2.23.1.18 | Display | -
6.1.2.23.1.19 | Number of impulses | yes/no | yes
6.1.2.23.1.20 | Leakage current measurement, total current | yes/no | yes
6.1.2.23.1.21 | Protection class | - | IP55 W
6.1.2.23.1.22 | Number of counters per three (3) 1-ph arresters | - | 3
6.1.2.23.2 | 132 kV Surge Arrester and Discharge Counter
6.1.2.23.2.1 | Manufacturer | - | -
6.1.2.23.2.2 | Place of manufacture | - | -
6.1.2.23.2.3 | Model designation | - | -
6.1.2.23.2.4 | Applicable standard | - | IEC 60071-1
IEC 60071-2
IEC 60099-4
IEC 60099-5
IEC 60529
IEC 60815
6.1.2.23.2.5 | Type | - | Outdoor, silicon-housed
6.1.2.23.2.6 | System data:
6.1.2.23.2.7 | · Nominal system voltage | kV | 132
6.1.2.23.2.8 | · Highest system voltage | kV | 145
6.1.2.23.2.9 | · System frequency | Hz | 50
6.1.2.23.2.10 | Rated voltage Ur | kV | 108
6.1.2.23.2.11 | Maximum continuous operating voltage Uc | kV | 86
6.1.2.23.2.12 | Rated discharge current | kA | 10 / 20 subject to calculation
6.1.2.23.2.13 | Thermal energy rating | kJ/kV | 10
6.1.2.23.2.14 | Separate earthing rod per SA, 150 mm2 | yes/no | yes
6.1.2.23.2.15 | Discharge Counter:
6.1.2.23.2.16 | Manufacturer | -
6.1.2.23.2.17 | Model designation | -
6.1.2.23.2.18 | Display | -
6.1.2.23.2.19 | Number of impulses | yes/no | yes
6.1.2.23.2.20 | Leakage current measurement, total current | yes/no | yes
6.1.2.23.2.21 | Protection class | - | IP 55 W
6.1.2.23.2.22 | Number of counters per three (3) 1-ph arresters | - | 3
6.1.2.24 | Transformer Main dimensions
6.1.2.24.1 | Total length x width x height | m
6.1.2.24.2 | Tank length x width x height | m
6.1.2.24.3 | Gross weight | kg
6.1.2.24.4 | Transport weight | kg
6.1.2.24.5 | Volume of oil | m3
6.1.2.24.6 | Weight of oil | kg
6.1.2.24.7 | Max. admitted accelerations in XYZ-directions during transport | g
6.1.2.25 | Tests
6.1.2.25.1 | Tests according to VII-5 Technical Specification | yes/no | yes
6.1.3 | Power Transformer 132/33 kV
6.1.3.1 | General Data
6.1.3.1.1 | Manufacturer | -
6.1.3.1.2 | Place of manufacture | -
6.1.3.1.3 | Applicable standard | - | IEC 60076 etc., as per VII-5 Technical Specifications
6.1.3.1.4 | 6 Sigma Quality Certification for Transformer Manufacturing Facilities | Yes/no | No
6.1.3.1.5 | Painting as per ISO 12944 C5-M | Yes/no | Yes
6.1.3.1.6 | Service altitude | m | <1000
6.1.3.1.7 | Ambient temperature (max.) | °C | 50
6.1.3.1.8 | Type | - | Power Transformer three-Phase
6.1.3.1.9 | Rated voltage | kV | 132/33
6.1.3.1.10 | Vector group | - | YNyn0+d
6.1.3.1.11 | Type of Cooling |  | ONAN/ONAF
6.1.3.1.12 | Type of insulation: | - | -
6.1.3.1.13 | · primary | - | Uniform
6.1.3.1.14 | · secondary |  | Uniform
6.1.3.1.15 | · tertiary | - | Uniform
6.1.3.1.16 | Location of use | - | outdoor
6.1.3.1.17 | Tank type | - | Upper flange
6.1.3.1.18 | Max noise level (LPA) - according to IEC 60076-10 - at a measuring distance of 2m with all forced cooling in operation | dB (A) | 70
6.1.3.1.19 | Rated frequency | Hz | 50
6.1.3.2 | Characteristics of magnetic circuit
6.1.3.2.1 | Type | - | Core type
6.1.3.2.2 | Material | - | Cold rolled grain silicon steel
6.1.3.2.3 | Maximum flux density at rated voltage and frequency | T | ≤1,65
6.1.3.3 | Temperature rise
6.1.3.3.1 | Top oil | K | 50
6.1.3.3.2 | Average winding | K | 55
6.1.3.3.3 | Hot spot winding | K | 68
6.1.3.4 | Rated power
6.1.3.4.1 | · ONAN | MVA | 24
6.1.3.4.2 | · ONAF | MVA | 30
6.1.3.5 | Rated withstand voltages for transformer windings
6.1.3.5.1 | 132 kV winding (Um=145 kV):
6.1.3.5.2 | · Rated lightning impulse withstand voltage | kVpeak | 650
6.1.3.5.3 | · Rated short-duration induced or separate source AC withstand voltage | kVrms | 275
6.1.3.5.4 | 33 kV winding (Um=36kV):
6.1.3.5.5 | · Rated lightning impulse withstand voltage | kVpeak | 170
6.1.3.5.6 | · Rated short-duration induced or separate source AC withstand voltage | kVrms | 70
6.1.3.5.7 | Neutral 132 kV winding (Um=52 kV):
6.1.3.5.8 | · Rated lightning impulse withstand voltage | kVpeak | N/A
6.1.3.5.9 | · Rated short-duration induced or separate source AC withstand voltage | kVrms | N/A
6.1.3.5.10 | Neutral 33 kV winding (Um=36 kV):
6.1.3.5.11 | · Rated lightning impulse withstand voltage | kVpeak | 170
6.1.3.5.12 | · Rated short-duration induced or separate source AC withstand voltage | kVrms | 70
6.1.3.6 | Short circuit level (3 s) of the system
6.1.3.6.1 | · 132 kV level | kA | 40
6.1.3.6.2 | · 33 kV level | kA | 25
6.1.3.7 | Impedance voltage in % at 75°C winding temperatureat full loading, ONAF, on:
6.1.3.7.1 | Nominal tap | % | 10.5
6.1.3.8 | Oil characteristics
6.1.3.8.1 | Mineral oil standard | - | IEC 60296
6.1.3.8.2 | Corrosive Sulphur test |  | IEC 62535
ASTM D 1275 method B
6.1.3.8.3 | Dryness of the oil after on-site installation |  | Water Content ≤5ppm
6.1.3.8.4 | Inhibited | Yes / No
6.1.3.8.5 | Manufacturer | -
6.1.3.8.6 | Oil type | inhibited/
6.1.3.8.7 | Type designation | -
6.1.3.8.8 | Minimum flash point | °C | 140
6.1.3.8.9 | Viscosity at 80°C | mm²/s
6.1.3.8.10 | Max. dielectric strength (1min.) | kV
6.1.3.8.11 | Total oil required | l
6.1.3.8.12 | Tests according to VII-5 Technical Specifications | yes/no | yes
6.1.3.9 | Bushings
6.1.3.9.1 | Applicable standard | - | IEC 60137
6.1.3.10 | 132 kV bushing | -
6.1.3.10.1 | · Manufacturer
6.1.3.10.2 | · Place of manufacture | -
6.1.3.10.3 | Type of bushing | - | RIP or RIS
6.1.3.10.4 | Type of bushing insulator | - | silicon
6.1.3.10.5 | Type designation | -
6.1.3.10.6 | Highest rated voltage | kV | 145
6.1.3.10.7 | Rated current | A | 800
6.1.3.10.8 | Rated thermal short time current (3 s) | kA | 40
6.1.3.10.9 | Rated dynamic current | kA | 100
6.1.3.10.10 | Minimum Unified Specific Creepage Distance (USCD) | mm/kV | 43.3
6.1.3.10.11 | Rated lightning impulse withstand voltage | kVpeak | 650
6.1.3.10.12 | Power frequency withstand voltage (dry) | kVrms | 275
6.1.3.11 | 33 kV bushing | -
6.1.3.11.1 | · Manufacturer
6.1.3.11.2 | · Place of manufacture | -
6.1.3.11.4 | Type of bushing insulator | - | porcelain
6.1.3.11.5 | Type designation | -
6.1.3.11.6 | Highest rated voltage | kV | 36
6.1.3.11.7 | Rated current | A | 800
6.1.3.11.8 | Rated thermal short time current (3 s) | kA | 40
6.1.3.11.9 | Rated dynamic current | kA | 100
6.1.3.11.10 | Minimum Unified Specific Creepage Distance (USCD) | mm/kV | 43.3
6.1.3.11.11 | Rated lightning impulse withstand voltage | kVpeak | 170
6.1.3.11.12 | Power frequency withstand voltage (dry) | kVrms | 70
6.1.3.12 | Neutral bushing 132 kV | -
6.1.3.12.1 | Manufacturer
6.1.3.12.2 | Place of manufacture | -
6.1.3.12.3 | Type of bushing | - | RIP or RIS
6.1.3.12.4 | Type of bushing insulator | - | silicon
6.1.3.12.5 | Type designation | -
6.1.3.12.6 | Highest rated voltage | kV | 52
6.1.3.12.7 | Rated current | A | 800
6.1.3.12.8 | Rated thermal short time current (3 s) | kA | 40
6.1.3.12.9 | Rated dynamic current | kA | 100
6.1.3.12.10 | Minimum Unified Specific Creepage Distance (USCD) | mm/kV | 43.3
6.1.3.12.11 | Rated lightning impulse withstand voltage | kVpeak | 250
6.1.3.12.12 | Power frequency withstand voltage (dry) | kVrms | 95
6.1.3.12.13 | Minimum cantilever withstand load | N | 500
6.1.3.13 | Neutral bushing 33 kV | -
6.1.3.13.1 | Manufacturer
6.1.3.13.2 | Place of manufacture | -
6.1.3.13.3 | Type of bushing insulator | - | porcelain
6.1.3.13.4 | Type designation | -
6.1.3.13.5 | Highest rated voltage | kV | 36
6.1.3.13.6 | Rated current | A | 800
6.1.3.13.7 | Rated thermal short time current (3 s) | kA | 40
6.1.3.13.8 | Rated dynamic current | kA | 100
6.1.3.13.9 | Minimum Unified Specific Creepage Distance (USCD) | mm/kV | 43.3
6.1.3.13.10 | Rated lightning impulse withstand voltage | kVpeak | 170
6.1.3.13.11 | Power frequency withstand voltage (dry) | kVrms | 70
6.1.3.13.12 | Minimum cantilever withstand load | N | 500
6.1.3.14 | Bushing current transformers
6.1.3.14.1 | 132 kV:
6.1.3.14.2 | · Ratio | A | 150/300/1/1
6.1.3.14.3 | · Core 1 burden and accuracy | - | 5P20 30 VA
6.1.3.14.4 | · Core 2 burden and accuracy | - | 5P20 30 VA
6.1.3.14.5 | · Core 3 burden and accuracy | - | N/A
6.1.3.14.6 | 33 kV:
6.1.3.14.7 | · Ratio | A | 600/800/1
6.1.3.14.8 | · Core 1 burden and accuracy | - | 5P20 30 VA
6.1.3.14.9 | · Core 2 burden and accuracy | - | 5P20 30 VA
6.1.3.14.10 | · Core 3 burden and accuracy | - | N/A
6.1.3.14.11 | Neutral 132 kV side:
6.1.3.14.12 | · Ratio | A | 150/300/1
6.1.3.14.13 | · Core 1 burden and accuracy | - | 5P20 30 VA
6.1.3.14.14 | · Core 2 burden and accuracy | - | 5P20 30 VA
6.1.3.14.15 | Neutral 33 kV side:
6.1.3.14.16 | · Ratio | A | 600/800/1
6.1.3.14.17 | · Core 1 burden and accuracy | - | 5P20 30 VA
6.1.3.14.18 | · Core 2 burden and accuracy | - | 5P20 30 VA
6.1.3.15 | Cooling system
6.1.3.15.1 | Type of cooling | - | ONAN/ONAF
6.1.3.15.2 | Number of coolers | pcs
6.1.3.15.3 | Cooling operation | - | Auto/Manual
6.1.3.15.4 | Control voltage for cooling and heating | V AC | 230
6.1.3.15.5 | Supply voltage of protective devices | V DC | 220
6.1.3.15.6 | Supply voltage of fans and pumps | V AC | 230/400
6.1.3.15.7 | Power demand of fans | kW
6.1.3.15.8 | Power demand of oil pumps | kW
6.1.3.16 | No load current
6.1.3.16.1 | No load current | %
6.1.3.16.2 | Magnetic flux density at rated voltage and frequency | Tesla | Max 1,65
6.1.3.16.3 | Core losses | W/kg | Max 1,05
6.1.3.17 | Losses
6.1.3.17.1 | No load losses at nominal voltage position | kW
6.1.3.17.2 | No load losses at lowest tap position | kW
6.1.3.17.3 | No load losses at highest tap position | kW
6.1.3.17.4 | Load losses at nominal tap at ONAN: | kW
6.1.3.17.5 | Load losses at nominal tap at ONAF: | kW
6.1.3.18 | OLTC (On-load tap-changer)
6.1.3.18.1 | Manufacturer | - | MR Germany or ABB Sweden, or equivalent
6.1.3.18.2 | Type designation | -
6.1.3.18.3 | Applicable standard | - | IEC 60214-1
6.1.3.18.4 | Type | - | vacuum
6.1.3.18.5 | Tapping on 132 kV side | % | + 8 x 1,25
6.1.3.18.6 | Rated through current | A | -
6.1.3.18.7 | Rated short-time current:
6.1.3.18.8 | maximum (peak) | kA | -
6.1.3.18.9 | 3 seconds | kA | -
6.1.3.18.10 | Rated power frequency withstand voltage | kVrms | -
6.1.3.18.11 | Rated lightning impulse withstand voltage | kVpeak | -
6.1.3.18.12 | Rated operations duty (min.) | - | 600,000
6.1.3.19 | Automatic Voltage Regulation
6.1.3.19.1 | Manufacturer | -
6.1.3.19.2 | Type / designation
6.1.3.19.3 | Sensitivity | -%,+% | 0,4 to 6% of transformer voltage
6.1.3.19.4 | Response time | s | 0-15 sec to 4 min. referred to 1% deviation from desired value
6.1.3.19.5 | Range of set point adjustment | % of Un | 90 to 115% UN
6.1.3.19.6 | Current-responsive rising | % of Un | 0 to 16% UN
6.1.3.19.7 | Limitation of current effect | % of Un | 0 to 16% UN
6.1.3.19.8 | Overvoltage Umax | % of Un | 100 to 135% UN
6.1.3.19.9 | Under voltage Umin. | % of Un | 50 to 100% UN
6.1.3.19.10 | Under/Overcurrent Imin/max | x In | 60 to 120 IN
6.1.3.19.11 | Line drop compensation |  | Yes
6.1.3.19.12 | Parallel operation with other transformer | - | Yes
6.1.3.20 | Neutral Treatment
6.1.3.20.1 | Brought up to bushings and grounded | yes/no | yes
6.1.3.20.2 | Neutral surge arrester | yes/no | no
6.1.3.20.3 | Neutral disconnector | yes/no | no
6.1.3.20.4 | Neutral current transformer | yes/no | yes
6.1.3.20.5 | Solidly grounded | yes/no | yes
6.1.3.21 | Accessories
6.1.3.21.1 | Accessories according to VII-5 Technical Specification | yes/no | yes
6.1.3.21.2 | Online transformer condition monitoring system according to VII-5 Technical Specification | yes/no | no
6.1.3.22 | Marshalling kiosks
6.1.3.22.1 | Degree of protection | - | IP55
6.1.3.22.2 | Marshalling kiosks according to VII-5 Technical Specification | yes/no | yes
6.1.3.23 | Tank mounted Surge Arrestors
6.1.3.23.1 | 132 kV Surge Arrester and Discharge Counter
6.1.3.23.1.1 | Manufacturer | - | -
6.1.3.23.1.2 | Place of manufacture | - | -
6.1.3.23.1.3 | Model designation | - | -
6.1.3.23.1.4 | Applicable standard | - | IEC 60071-1
IEC 60071-2
IEC 60099-4
IEC 60099-5
IEC 60529
IEC 60815
6.1.3.23.1.5 | Type | - | Outdoor, silicon-housed
6.1.3.23.1.6 | System data:
6.1.3.23.1.7 | · Nominal system voltage | kV | 132
6.1.3.23.1.8 | · Highest system voltage | kV | 145
6.1.3.23.1.9 | · System frequency | Hz | 50
6.1.3.23.1.10 | Rated voltage Ur | kV | 108
6.1.3.23.1.11 | Maximum continuous operating voltage Uc | kV | 86
6.1.3.23.1.12 | Rated discharge current | kA | 10 / 20 subject to calculation
6.1.3.23.1.13 | Thermal energy rating | kJ/kV | 10
6.1.3.23.1.14 | Separate earthing rod per SA, 150 mm2 | yes/no | yes
6.1.3.23.1.15 | Discharge Counter:
6.1.3.23.1.16 | Manufacturer | -
6.1.3.23.1.17 | Model designation | -
6.1.3.23.1.18 | Display | -
6.1.3.23.1.19 | Number of impulses | yes/no | yes
6.1.3.23.1.20 | Leakage current measurement, total current | yes/no | yes
6.1.3.23.1.21 | Protection class | - | IP 55 W
6.1.3.23.1.22 | Number of counters per three (3) 1-ph arresters | - | 3
6.1.3.23.2 | 33 kV Surge Arrester
6.1.3.23.2.1 | Manufacturer | - | -
6.1.3.23.2.2 | Place of manufacture | - | -
6.1.3.23.2.3 | Model designation | - | -
6.1.3.23.2.4 | Applicable standard | - | IEC 60071-1
IEC 60071-2
IEC 60099-4
IEC 60099-5
IEC 60529
IEC 60815
6.1.3.23.2.5 | Type | - | Outdoor, silicon-housed
6.1.3.23.2.6 | System data:
6.1.3.23.2.7 | · Nominal system voltage | kV | 33
6.1.3.23.2.8 | · Highest system voltage | kV | 36
6.1.3.23.2.9 | · System frequency | Hz | 50
6.1.3.23.2.10 | Rated voltage Ur | kV | 27
6.1.3.23.2.11 | Maximum continuous operating voltage Uc | kV | 21
6.1.3.23.2.12 | Rated discharge current | kA | 10 / 20 subject to calculation
6.1.3.23.2.13 | Thermal energy rating | kJ/kV | 10
6.1.3.24 | Transformer Main dimensions
6.1.3.24.1 | Total length x width x height | m
6.1.3.24.2 | Tank length x width x height | m
6.1.3.24.3 | Gross weight | kg
6.1.3.24.4 | Transport weight | kg
6.1.3.24.5 | Volume of oil | m3
6.1.3.24.6 | Weight of oil | kg
6.1.3.24.7 | Max. admitted accelerations in XYZ-directions during transport | g
6.1.3.25 | Tests
6.1.3.25.1 | Tests according to VII-5 Technical Specification | yes/no | yes
6.1.4 | Power Transformer 33/11 kV
6.1.4.1 | General Data
6.1.4.1.1 | Manufacturer | -
6.1.4.1.2 | Place of manufacture | -
6.1.4.1.3 | Applicable standard | - | IEC 60076 etc., as per VII-5 Technical Specifications
6.1.4.1.4 | 6 Sigma Quality Certification for Transformer Manufacturing Facilities | Yes/no | No
6.1.4.1.5 | Painting as per ISO 12944 C5-M | Yes/no | Yes
6.1.4.1.6 | Service altitude | m | <1000
6.1.4.1.7 | Ambient temperature (max.) | °C | 50
6.1.4.1.8 | Type | - | Power Transformer three-Phase
6.1.4.1.9 | Rated voltage | kV | 33/11
6.1.4.1.10 | Vector group | - | Dyn11
6.1.4.1.11 | Type of Cooling |  | ONAN/ONAF
6.1.4.1.12 | Type of insulation: | - | -
6.1.4.1.13 | · primary | - | Uniform
6.1.4.1.14 | · secondary |  | Uniform
6.1.4.1.15 | Location of use | - | outdoor
6.1.4.1.16 | Tank type | - | Upper flange
6.1.4.1.17 | Max noise level (LPA) - according to IEC 60076-10 - at a measuring distance of 2m with all forced cooling in operation | dB (A) | <69
6.1.4.1.18 | Rated frequency | Hz | 50
6.1.4.2 | Characteristics of magnetic circuit
6.1.4.2.1 | Type | - | Core type
6.1.4.2.2 | Material | - | Cold rolled grain silicon steel
6.1.4.2.3 | Maximum flux density at rated voltage and frequency | T | ≤1,65
6.1.4.3 | Temperature rise
6.1.4.3.1 | Top oil | K | 50
6.1.4.3.2 | Average winding | K | 55
6.1.4.3.3 | Hot spot winding | K | 68
6.1.4.4 | Rated power
6.1.4.4.1 | · ONAN | MVA | 6
6.1.4.4.2 | · ONAF | MVA | 8
6.1.4.5 | Rated withstand voltages for transformer windings
6.1.4.5.1 | 33 kV winding (Um=36kV):
6.1.4.5.2 | · Rated lightning impulse withstand voltage | kVpeak | 170
6.1.4.5.3 | · Rated short-duration induced or separate source AC withstand voltage | kVrms | 70
6.1.4.5.4 | 11 kV winding (Um=12 kV):
6.1.4.5.5 | · Rated lightning impulse withstand voltage | kVpeak | 75
6.1.4.5.6 | · Rated short-duration induced or separate source AC withstand voltage | kVrms | 28
6.1.4.5.7 | Neutral winding (Um=11 kV):
6.1.4.5.8 | · Rated lightning impulse withstand voltage | kVpeak | 75
6.1.4.5.9 | · Rated short-duration induced or separate source AC withstand voltage | kVrms | 28
6.1.4.6 | Short circuit level (3 s) of the system
6.1.4.6.1 | · 33 kV level | kA | 25
6.1.4.6.2 | · 11 kV level | kA | -
6.1.4.7 | Impedance voltage in % at 75°C winding temperature on middle tap position at full loading, ONAF | % | 6
6.1.4.8 | Oil characteristics
6.1.4.8.1 | Mineral oil standard | - | IEC 60296
6.1.4.8.2 | Corrosive Sulphur test |  | IEC 62535
ASTM D 1275 method B
6.1.4.8.3 | Dryness of the oil after on-site installation |  | Water Content ≤5ppm
6.1.4.8.4 | Inhibited | Yes / No
6.1.4.8.5 | Manufacturer | -
6.1.4.8.6 | Oil type | inhibited/
6.1.4.8.7 | Type designation | -
6.1.4.8.8 | Minimum flash point | °C | 140
6.1.4.8.9 | Viscosity at 80°C | mm²/s
6.1.4.8.10 | Max. dielectric strength (1min.) | kV
6.1.4.8.11 | Total oil required | l
6.1.4.8.12 | Tests according to VII-5 Technical Specifications | yes/no | yes
6.1.4.9 | Bushings
6.1.4.9.1 | Applicable standard | - | IEC 60137
6.1.4.10 | 33 kV bushing | -
6.1.4.10.1 | · Manufacturer
6.1.4.10.2 | · Place of manufacture | -
6.1.4.11.3 | Type of bushing insulator | - | porcelain
6.1.4.10.3 | Type designation | -
6.1.4.10.4 | Highest rated voltage | kV | 36
6.1.4.10.5 | Rated current | A | 800
6.1.4.10.6 | Rated thermal short time current (3 s) | kA | 40
6.1.4.10.7 | Rated dynamic current | kA | 100
6.1.4.10.8 | Minimum Unified Specific Creepage Distance (USCD) | mm/kV | 43.3
6.1.4.10.9 | Rated lightning impulse withstand voltage | kVpeak | 170
6.1.4.10.10 | Power frequency withstand voltage (dry) | kVrms | 70
6.1.4.11 | 11 kV bushing | -
6.1.4.11.1 | · Manufacturer
6.1.4.11.2 | · Place of manufacture | -
6.1.4.11.3 | Type of bushing insulator | - | porcelain
6.1.4.11.4 | Type designation | -
6.1.4.11.5 | Highest rated voltage | kV | 12
6.1.4.11.6 | Rated current | A | 800
6.1.4.11.7 | Rated thermal short time current (3 s) | kA | 40
6.1.4.11.8 | Rated dynamic current | kA | 100
6.1.4.11.9 | Minimum Unified Specific Creepage Distance (USCD) | mm/kV | 43.3
6.1.4.11.10 | Rated lightning impulse withstand voltage | kVpeak | 95
6.1.4.11.11 | Power frequency withstand voltage (dry) | kVrms | 28
6.1.4.12 | Neutral bushing 11 kV | -
6.1.4.12.1 | Manufacturer
6.1.4.12.2 | Place of manufacture | -
6.1.4.12.3 | Type of bushing insulator | - | porcelain
6.1.4.12.4 | Type designation | -
6.1.4.12.5 | Highest rated voltage | kV | 12
6.1.4.12.6 | Rated current | A | 800
6.1.4.12.7 | Rated thermal short time current (3 s) | kA | 40
6.1.4.12.8 | Rated dynamic current | kA | 100
6.1.4.12.9 | Minimum Unified Specific Creepage Distance (USCD) | mm/kV | 43.3
6.1.4.12.10 | Rated lightning impulse withstand voltage | kVpeak | 95
6.1.4.12.11 | Power frequency withstand voltage (dry) | kVrms | 28
6.1.4.13 | Bushing current transformers
6.1.4.13.1 | 33 kV:
6.1.4.13.2 | · Ratio | A | 150-300/1
6.1.4.13.3 | · Core 1 burden and accuracy | - | 5P20 30 VA
6.1.4.13.4 | · Core 2 burden and accuracy | - | 5P20 30 VA
6.1.4.13.5 | · Core 3 burden and accuracy | - | N/A
6.1.4.13.6 | 11 kV:
6.1.4.13.7 | · Ratio | A | 450-900/1
6.1.4.13.8 | · Core 1 burden and accuracy | - | 5P20 30 VA
6.1.4.13.9 | · Core 2 burden and accuracy | - | 5P20 30 VA
6.1.4.13.10 | · Core 3 burden and accuracy | - | N/A
6.1.4.13.11 | Neutral 11 kV side:
6.1.4.13.12 | · Ratio | A | 450-900/1
6.1.4.13.13 | · Core 1 burden and accuracy | - | 5P20 30 VA
6.1.4.13.14 | · Core 2 burden and accuracy | - | 5P20 30 VA
6.1.4.14 | Cooling system
6.1.4.14.1 | Type of cooling | - | ONAN/ONAF
6.1.4.14.2 | Number of coolers | pcs
6.1.4.14.3 | Cooling operation | - | Auto/Manual
6.1.4.14.4 | Control voltage for cooling and heating | V AC | 230
6.1.4.14.5 | Supply voltage of protective devices | V DC | 220
6.1.4.14.6 | Supply voltage of fans and pumps | V AC | 230/400
6.1.4.14.7 | Power demand of fans | kW
6.1.4.14.8 | Power demand of oil pumps | kW
6.1.4.15 | No load current
6.1.4.15.1 | No load current | %
6.1.4.15.2 | Magnetic flux density at rated voltage and frequency | Tesla | ≤1,65
6.1.4.15.3 | Core losses | W/kg | Max 1,05
6.1.4.16 | Losses
6.1.4.16.1 | No load losses at nominal voltage position | kW
6.1.4.16.2 | No load losses at lowest tap position | kW
6.1.4.16.3 | No load losses at highest tap position | kW
6.1.4.16.4 | Load losses at nominal tap at ONAN: | kW
6.1.4.16.5 | Load losses at nominal tap at ONAF: | kW
6.1.4.17 | OLTC (On-load tap-changer)
6.1.4.17.1 | Manufacturer | - | MR Germany or ABB Sweden, or equivalent
6.1.4.17.2 | Type designation | -
6.1.4.17.3 | Applicable standard | - | IEC 60214-1
6.1.4.17.4 | Type | - | vacuum
6.1.4.17.5 | Tapping on 132 kV side | % | + 8 x 1,25
6.1.4.17.6 | Rated through current | A | -
6.1.4.17.7 | Rated short-time current:
6.1.4.17.8 | maximum (peak) | kA | -
6.1.4.17.9 | 3 seconds | kA | -
6.1.4.17.10 | Rated power frequency withstand voltage | kVrms | -
6.1.4.17.11 | Rated lightning impulse withstand voltage | kVpeak | -
6.1.4.17.12 | Rated operations duty (min.) | - | 600,000
6.1.4.18 | Automatic Voltage Regulation
6.1.4.18.1 | Manufacturer | -
6.1.4.18.2 | Type / designation
6.1.4.18.3 | Sensitivity | -%,+% | 0,4 to 6% of transformer voltage
6.1.4.18.4 | Response time | s | 0-15 sec to 4 min. referred to 1% deviation from desired value
6.1.4.18.5 | Range of set point adjustment | % of Un | 90 to 115% UN
6.1.4.18.6 | Current-responsive rising | % of Un | 0 to 16% UN
6.1.4.18.7 | Limitation of current effect | % of Un | 0 to 16% UN
6.1.4.18.8 | Overvoltage Umax | % of Un | 100 to 135% UN
6.1.4.18.9 | Under voltage Umin. | % of Un | 50 to 100% UN
6.1.4.18.10 | Under/Overcurrent Imin/max | x In | 60 to 120 IN
6.1.4.18.11 | Line drop compensation |  | Yes
6.1.4.18.12 | Parallel operation with other transformer | - | Yes
6.1.4.19 | Neutral Treatment
6.1.4.19.1 | Brought up to bushings and grounded | yes/no | yes
6.1.4.19.2 | Neutral surge arrester | yes/no | no
6.1.4.19.3 | Neutral disconnector | yes/no | no
6.1.4.19.4 | Neutral current transformer | yes/no | yes
6.1.4.19.5 | Solidly grounded | yes/no | yes
6.1.4.20 | Accessories
6.1.4.20.1 | Accessories according to VII-5 Technical Specification | yes/no | yes
6.1.4.20.2 | Online transformer condition monitoring system according to VII-5 Technical Specification | yes/no | no
6.1.4.21 | Marshalling kiosks
6.1.4.21.1 | Degree of protection | - | IP55
6.1.4.21.2 | Marshalling kiosks according to VII-5 Technical Specification | yes/no | yes
6.1.4.22 | Tank mounted Surge Arrestors
6.1.4.22.1 | 33 kV Surge Arrester
6.1.4.22.1.1 | Manufacturer | - | -
6.1.4.22.1.2 | Place of manufacture | - | -
6.1.4.22.1.3 | Model designation | - | -
6.1.4.22.1.4 | Applicable standard | - | IEC 60071-1
IEC 60071-2
IEC 60099-4
IEC 60099-5
IEC 60529
IEC 60815
6.1.4.22.1.5 | Type | - | Outdoor, silicon-housed
6.1.4.22.1.6 | System data:
6.1.4.22.1.7 | · Nominal system voltage | kV | 33
6.1.4.22.1.8 | · Highest system voltage | kV | 36
6.1.4.22.1.9 | · System frequency | Hz | 50
6.1.4.22.1.10 | Rated voltage Ur | kV | 27
6.1.4.22.1.11 | Maximum continuous operating voltage Uc | kV | 21
6.1.4.22.1.12 | Rated discharge current | kA | 10 / 20 subject to calculation
6.1.4.22.1.13 | Thermal energy rating | kJ/kV | 10
6.1.4.22.2 | 11 kV Surge Arrester
6.1.4.22.2.1 | Manufacturer | - | -
6.1.4.22.2.2 | Place of manufacture | - | -
6.1.4.22.2.3 | Model designation | - | -
6.1.4.22.2.4 | Applicable standard | - | IEC 60071-1
IEC 60071-2
IEC 60099-4
IEC 60099-5
IEC 60529
IEC 60815
6.1.4.22.2.5 | Type | - | Outdoor, silicon-housed
6.1.4.22.2.6 | System data:
6.1.4.22.2.7 | · Nominal system voltage | kV | 11
6.1.4.22.2.8 | · Highest system voltage | kV | 12
6.1.4.22.2.9 | · System frequency | Hz | 50
6.1.4.22.2.10 | Rated voltage Ur | kV | 9
6.1.4.22.2.11 | Maximum continuous operating voltage Uc | kV | 7.2
6.1.4.22.2.12 | Rated discharge current | kA | 10 / 20 subject to calculation
6.1.4.22.2.13 | Thermal energy rating | kJ/kV | 10
6.1.4.23 | TransformerMain dimensions
6.1.4.23.1 | Total length x width x height | m
6.1.4.23.2 | Tank length x width x height | m
6.1.4.23.3 | Gross weight | kg
6.1.4.23.4 | Transport weight | kg
6.1.4.23.5 | Volume of oil | m3
6.1.4.23.6 | Weight of oil | kg
6.1.4.23.7 | Max. admitted accelerations in XYZ-directions during transport | g
6.1.4.24 | Tests
6.1.4.24.1 | Tests according to VII-5 Technical Specification | yes/no | yes
6.2 | Auxiliary Transformers
6.2.1 | Auxiliary Transformer 33/0.4 kV for Damauli
6.2.1.1 | General Data
6.2.1.1.1 | Manufacturer | -
6.2.1.1.2 | Place of manufacture | -
6.2.1.1.3 | Applicable standard | - | IEC 60076 etc., as per VII-5 Technical Specification
6.2.1.1.4 | Service altitude: | m | <1000
6.2.1.1.5 | Ambient temperature | °C | 50
6.2.1.1.6 | Transformer winding configuration | - | 2-winding
6.2.1.1.7 | Nominal voltage | kV | 33/0,4
6.2.1.1.8 | Rated maximum voltage | kV
6.2.1.1.9 | Type of insulation | - | 3-phase oil immersed, uniform
6.2.1.1.10 | Location of use | - | outdoor
6.2.1.1.11 | Tank type | - | Upper flange
6.2.1.1.12 | Vector group | - | Dyn11
6.2.1.1.13 | Type of cooling | - | ONAN
6.2.1.1.14 | Construction Type | - | hermetically sealed
6.2.1.1.15 | Max noise level (LPA) - according to IEC 60076-10 - at a measuring distance of 2m with all forced cooling in operation | dB (A) | 60
6.2.1.1.16 | Rated frequency | Hz | 50
6.2.1.1.17 | Rated power: | kVA | 1250
6.2.1.2 | Characteristics of magnetic circuit
6.2.1.2.1 | Type | - | Core type
6.2.1.2.2 | Material | - | Cold rolled grain silicon steel
6.2.1.2.3 | Maximum flux density at rated voltage and frequency | T | ≤1,65
6.2.1.3 | Temperature rise
6.2.1.2.3 | Top oil: | K | 50
6.2.1.2.4 | Average winding: | K | 55
6.2.1.2.5 | Hot spot winding: | K | 68
6.2.1.3 | Rated withstand voltages for transformer windings
6.2.1.3.1 | 33 kV winding (Um=36 kV):
6.2.1.3.2 | · Rated lightning impulse withstand voltage | kVpeak | 170
6.2.1.3.3 | · Rated short-duration induced or separate source AC withstand voltage | kVrms | 70
6.2.1.3.4 | 0.4 kV winding:
6.2.1.3.5 | Power frequency withstand voltage | kVrms | 1,1
6.2.1.4 | Rated nominal current
6.2.1.4.1 | Rated nominal current MV | A
| Rated nominal current LV | A
6.2.1.5 | Impedance voltage in % at 75°C winding temperature at full loading
6.2.1.5.1 | MV-LV | % | 6
6.2.1.6 | Off load tap changer
6.2.1.6.1 | Voltage ratio and taps | % | +/-2 x 2,5%
6.2.1.6.2 | Installation | - | on the MV winding
6.2.1.6.3 | Dial type indicator for the selected tap position | yes/no | yes
6.2.1.7 | Accessories
6.2.1.7.1 | Accessories according to the Tender Documents | yes/no | yes
6.2.1.8 | No load current
6.2.1.8.1 | No load current | %
6.2.1.8.2 | Magnetic flux density at rated voltage and frequency | Tesla | Max 1,65
6.2.1.8.3 | Core losses | W/kg | Max 1,05
6.2.1.9 | Losses
6.2.1.9.1 | No load losses at nominal voltage position | kW
6.2.1.9.2 | Load losses at nominal tap at ONAN: | kW
6.2.1.10 | Tank mounted Surge 33 kV Arrestors
6.2.1.10.1 | Manufacturer | - | -
6.2.1.10.2 | Place of manufacture | - | -
6.2.1.10.3 | Model designation | - | -
6.2.1.10.4 | Applicable standard | - | IEC 60071-1
IEC 60071-2
IEC 60099-4
IEC 60099-5
IEC 60529
IEC 60815
6.2.1.10.5 | Type | - | Outdoor, silicon-housed
6.2.1.10.6 | System data:
6.2.1.10.7 | · Nominal system voltage | kV | 33
6.2.1.10.8 | · Highest system voltage | kV | 36
6.2.1.10.9 | · System frequency | Hz | 50
6.2.1.10.10 | Rated voltage Ur | kV | 27
6.2.1.10.11 | Maximum continuous operating voltage Uc | kV | 21
6.2.1.10.12 | Rated discharge current | kA | 10 / 20 subject to calculation
6.2.1.10.13 | Thermal energy rating | kJ/kV | 10
6.2.1.11 | Transformer Main dimensions
6.2.1.11.1 | Total length x width x height | m
6.2.1.11.2 | Gross weight | kg
6.2.1.11.3 | Volume of oil | m3
6.2.1.11.4 | Weight of oil | kg
6.2.1.12 | Tests
6.2.1.12.1 | Tests according to VII-5 Technical Specification | yes/no | yes
6.2.2 | Earthing Auxiliary Transformer 33/0.4 kV for Lekhnath
6.2.2.1 | General Data
6.2.2.1.1 | Manufacturer | -
6.2.2.1.2 | Place of manufacture | -
6.2.2.1.3 | Applicable standard | - | IEC 60076 etc., as per VII-5 Technical Specification
6.2.2.1.4 | Service altitude: | m | <1000
6.2.2.1.5 | Ambient temperature | °C | 40
6.2.2.1.6 | Transformer winding configuration | - | 2-winding
6.2.2.1.7 | Nominal voltage | kV | 33/0,4
6.2.2.1.8 | Rated maximum voltage | kV
6.2.2.1.9 | Type of insulation | - | 3-phase oil immersed, uniform
6.2.2.1.10 | Location of use | - | outdoor
6.2.2.1.11 | Tank type | - | Upper flange
6.2.2.1.12 | Vector group | - | ZNyn11
6.2.2.1.13 | Type of cooling | - | ONAN
6.2.2.1.14 | Construction Type | - | hermetically sealed
6.2.2.1.15 | Max noise level (LPA) - according to IEC 60076-10 - at a measuring distance of 2m with all forced cooling in operation | dB (A) | 60
6.2.2.1.16 | Rated frequency | Hz | 50
6.2.2.1.17 | Rated power: | kVA | 630
6.2.2.2 | Characteristics of magnetic circuit
6.2.2.2.1 | Type | - | Core type
6.2.2.2.2 | Material | - | Cold rolled grain silicon steel
6.2.2.2.3 | Maximum flux density at rated voltage and frequency | T | ≤1,65
6.2.2.3 | Temperature rise
6.2.2.2.3 | Top oil: | K | 60
6.2.2.2.4 | Average winding: | K | 65
6.2.2.2.5 | Hot spot winding: | K | 78
6.2.2.3 | Rated withstand voltages for transformer windings
6.2.2.3.1 | 33 kV winding (Um=36 kV):
6.2.2.3.2 | · Rated lightning impulse withstand voltage | kVpeak | 170
6.2.2.3.3 | · Rated short-duration induced or separate source AC withstand voltage | kVrms | 70
6.2.2.3.4 | 0.4 kV winding:
6.2.2.3.5 | Power frequency withstand voltage | kVrms | 1,1
6.2.2.4 | Rated nominal current
6.2.2.4.1 | Rated nominal current MV | A
| Rated nominal current LV | A
6.2.2.5 | Impedance voltage in % at 75°C winding temperature at full loading
6.2.2.5.1 | MV-LV | % | 6
6.2.2.5.2 | Zero sequence current primary side | A | 300
6.2.2.5.3 | Zero sequence impedance primay side | Ohm
6.2.2.6 | Off load tap changer
6.2.2.6.1 | Voltage ratio and taps | % | +/-2 x 2,5%
6.2.2.6.2 | Installation | - | on the MV winding
6.2.2.6.3 | Dial type indicator for the selected tap position | yes/no | yes
6.2.2.7 | Accessories
6.2.2.7.1 | Accessories according to the Tender Documents | yes/no | yes
6.2.2.8 | No load current
6.2.2.8.1 | No load current | %
6.2.2.8.2 | Magnetic flux density at rated voltage and frequency | Tesla | Max 1,65
6.2.2.8.3 | Core losses | W/kg | Max 1,05
6.2.2.9 | Losses
6.2.2.9.1 | No load losses at nominal voltage position | kW
6.2.2.9.2 | Load losses at nominal tap at ONAN: | kW
6.2.2.10 | Bushing current transformers
6.2.2.10.1 | Neutral 33 kV side:
6.2.2.10.2 | · Ratio | A | 300/1
6.2.2.10.3 | · Core 1 burden and accuracy | - | 5P20 30 VA
6.2.2.11 | Tank mounted Surge 33 kV Arrestors
6.2.2.11.1 | Manufacturer | - | -
6.2.2.11.2 | Place of manufacture | - | -
6.2.2.11.3 | Model designation | - | -
6.2.2.11.4 | Applicable standard | - | IEC 60071-1
IEC 60071-2
IEC 60099-4
IEC 60099-5
IEC 60529
IEC 60815
6.2.2.11.5 | Type | - | Outdoor, silicon-housed
6.2.2.11.6 | System data:
6.2.2.11.7 | · Nominal system voltage | kV | 33
6.2.2.11.8 | · Highest system voltage | kV | 36
6.2.2.11.9 | · System frequency | Hz | 50
6.2.2.11.10 | Rated voltage Ur | kV | 27
6.2.2.11.11 | Maximum continuous operating voltage Uc | kV | 21
6.2.2.11.12 | Rated discharge current | kA | 10 / 20 subject to calculation
6.2.2.11.13 | Thermal energy rating | kJ/kV | 10
6.2.2.12 | Transformer Main dimensions
6.2.2.12.1 | Total length x width x height | m
6.2.2.12.2 | Gross weight | kg
6.2.2.12.3 | Volume of oil | m3
6.2.2.12.4 | Weight of oil | kg
6.2.2.13 | Tests
6.2.2.13.1 | Tests according to VII-5 Technical Specification | yes/no | yes

## 7. AC&DC
Technical Data Sheets
BIDDER’S / CONTRACTOR’S GUARANTEED DATA |  | Unit | Data required | Data offered
No. | Description
7 | AC & DC Installations
7.1 | LV AC Main Switchgear
7.1.1 | General data
7.1.1.1 | Manufacturer | -
7.1.1.2 | Place of manufacture | -
7.1.1.3 | Model designation | -
7.1.1.4 | Applicable standard | - | IEC 61439, IEC 60947 etc. as per Employer's Requirements
7.1.1.5 | Internal separation Incomer / Buscouplers | - | Form 4b
7.1.1.6 | Internal separation outgoing feeders | - | Form 3b
7.1.1.7 | Location of installation | - | indoor
7.1.1.8 | Number of phases | - | 3+N+PE
7.1.1.9 | Number of busbars | - | 1
7.1.1.10 | Nominal voltage | kV | 0.4
7.1.1.11 | Rated voltage | kV | 1
7.1.1.12 | Rated frequency | Hz | 50
7.1.1.13 | Rated power frequency withstand voltage | kVrms | 1.1
7.1.1.14 | Rated lightning impulse withstand voltage (1.2/50 µs) | kVpeak | 3.3
7.1.1.15 | Rated current (Lekhnath / Damauli) | A | ≥1000 / ≥2000
7.1.1.16 | Rated short-time current, 3 s (Lekhnath / Damauli) | kA | ≥25 / ≥31.5
7.1.1.17 | Rated peak withstand current (Lekhnath / Damauli) | kA | ≥62.5 / ≥78.75
7.1.1.18 | Power supply for auxiliary contacts | V DC | 220
7.1.1.19 | Power supply for heaters | V AC | 230
7.1.1.20 | Degree of Protection | - | IP54
7.1.1.21 | Instruments and accessories in accordance with the Employer's Requirements | yes/no | yes
7.1.2 | Circuit breaker for incomers and buscoupler
7.1.2.1 | Manufacturer | -
7.1.2.2 | Place of manufacture | -
7.1.2.3 | Model designation | -
7.1.2.4 | Type | - | Air circuit breaker (ACB)
7.1.2.5 | Type of drive | - | Spring, motor & manual charging
7.1.2.6 | Power supply for drive | V AC | 230
7.1.2.7 | Integrated protection | yes/no | yes
7.1.2.8 | Interface to SCADA | yes/no | yes
7.1.3 | Outgoing feeders
7.1.3.1 | Manufacturer | -
7.1.3.2 | Place of manufacture | -
7.1.3.3 | Model designation | -
7.1.3.4 | Type | - | MCCB
7.1.3.5 | Operation | - | manual
7.1.3.6 | Auxilairy contacts | yes/no | yes
7.1.4 | Current transformers
7.1.4.1 | Rated primary current:
7.1.4.2 | Aux transformer feeder incomers | A | ≥1000 / ≥2000
7.1.4.3 | Diesel generator Set feeder incomer
7.1.4.4 | Lekhnath | A | 150
7.1.4.5 | Damauli | A | 250
7.1.4.6 | Secondary currents | A | 1
7.1.4.7 | Number of secondary windings | - | 2
7.1.4.8 | Accuracy class | - | 10 VA Cl. 0,5
7.1.3 | Voltage transformer
7.1.3.1 | Rated primary voltage | V | 400/√3
7.1.3.2 | Secondary voltage | V | 110/√3
7.1.3.3 | Number of secondary windings | - | 1
7.1.3.4 | Accuracy class | - | 20VACl. 0,5
7.1.4 | Automatic Transfer device
7.1.4.1 | Manufacturer | -
7.1.4.2 | Type | -
7.1.4.3 | Function display | yes/no | yes
7.1.4.4 | Programmable | yes/no | yes
7.1.4.5 | Local/remote switch | yes/no | yes
7.1.4.6 | Operation via display and SCADA | yes/no | yes
7.1.4.7 | Trigger circuit supervision | yes/no | yes
7.1.4.8 | Measurement of operation values (U/I/f.) | yes/no | yes
7.1.5 | Main dimensions
7.1.5.1 | Number of individual panels | -
7.1.5.2 | Dimensions of the individual panels L x W x H | mm
7.1.5.3 | Weight of the individual panels | kg
7.1.6 | Tests
7.1.6.1 | Tests as per the relevant standards and Employer's Requirements | yes/no | yes
7.2 | LV AC Distribution Panels
7.2.1 | General data
7.2.1.1 | Manufacturer | -
7.2.1.2 | Place of manufacture | -
7.2.1.3 | Model designation | -
7.2.1.4 | Applicable standard | - | IEC 61439, IEC 60947 etc. as per Employer's Requirements
7.2.1.5 | Internal separation | - | Form 2b
7.2.1.6 | Location of installation | - | indoor
7.2.1.7 | Number of phases | - | 3+N+PE
7.2.1.8 | Number of busbars | - | 1
7.2.1.9 | Nominal voltage | kV | 0.4
7.2.1.10 | Rated voltage | kV | 1
7.2.1.11 | Rated frequency | Hz | 50
7.2.1.12 | Rated power frequency withstand voltage | kVrms | 1.1
7.2.1.13 | Rated lightning impulse withstand voltage (1.2/50 µs) | kVpeak | 3.3
7.2.1.14 | Rated short-time current, 1 s | kA | 25
7.2.1.15 | Rated peak withstand current | kA | 62.5
7.2.1.16 | Rated current | A | 160
7.2.1.17 | Degree of Protection | - | IP54
7.2.1.18 | Instruments and accessories as per the Employer's Requirements | yes/no | yes
7.2.2 | Automatic Transfer device
7.2.2.1 | Manufacturer | -
7.2.2.2 | Type | -
7.2.2.3 | Function display | yes/no | yes
7.2.2.4 | Programmable | yes/no | yes
7.2.2.5 | Local/remote switch | yes/no | yes
7.2.2.6 | Operation via MMD and SCADA | yes/no | yes
7.2.2.7 | Trigger circuit supervision | yes/no | yes
7.2.2.8 | Measurement of operation values (U/I/f.) | yes/no | yes
7.2.3 | Main dimensions
7.2.3.1 | Number of individual panels | -
7.2.3.2 | Dimensions of the individual panels L x W x H | mm
7.2.3.3 | Weight of the individual panels | kg
7.2.4 | Tests
7.2.4.1 | Tests as per the relevant standards and Employer's Requirements | yes/no | yes
7.3 | Main 220 V DC Switchgear
7.3.1 | General data
7.3.1.1 | Manufacturer | -
7.3.1.2 | Place of manufacture | -
7.3.1.3 | Model designation | -
7.3.1.4 | Applicable standard | - | IEC 61439, IEC 60947 etc. as per Employer's Requirements
7.3.1.5 | Internal separation outgoing feeders | - | Form 2b
7.3.1.6 | Location of installation | - | indoor
7.3.1.7 | Number of phases | - | L+/L-
7.3.1.8 | Number of busbars | - | 1
7.3.1.9 | Nominal voltage | V DC | 220
7.3.1.10 | Rated power frequency withstand voltage | kV rms | 1.1
7.3.1.11 | Rated short-time current, 3s | kA | 3.3
7.3.1.12 | Rated peak withstand current | kA
7.3.1.13 | Rated current for busbar | A
7.3.1.14 | Power supply for heaters | VAC | 230
7.3.1.15 | Insulation resistance | MΩ | 0.5
7.3.1.16 | Degree of protection | - | IP54
7.3.1.17 | Instruments and accessories in accordance with the Employer's Requirements | yes/no | yes
7.3.2 | Main dimensions
7.3.2.1 | Number of individual panels | -
7.3.2.2 | Dimensions of the individual panels L x W x H | mm
7.3.2.3 | Weight of the individual panels | kg
7.3.3 | Tests
7.3.3.1 | Tests as per the relevant standards and Employer's Requirements | yes/no | yes
7.4 | 220V DC Battery Charger
7.4.1 | Manufacturer | -
7.4.2 | Place of manufacture | -
7.4.3 | Applicable standard | - | IEC 60146
7.4.4 | Location of installation | - | indoor
7.4.5 | Type of controls | - | thyristor control
7.4.6 | Type of cooling | - | self-ventilating
7.4.7 | Rated voltage primary | V | 400
7.4.8 | Rated voltage secondary | V DC | 220±10%
7.4.9 | Rated current | A
7.4.10 | Rated capacity | kVA
7.4.11 | IP protection | IP | 43
7.4.12 | Mounted in metal cabinet | - | yes
7.4.13 | Charging characteristics:
7.4.14 | - Constant voltage range | V
7.4.15 | - Continuous charging voltage per cell and tolerances | V +/-
7.4.16 | - Residual ripple (without connected battery) | % | < 5 % rms
7.4.17 | - Voltage stability with both rectifiers connected to the load | % | +/-1,5
7.4.18 | Noise level | dB (A)
7.4.19 | Blocking diodes in the output circuit of each rectifier | yes/no | yes
7.4.20 | Main dimensions L x W x H | mm
7.4.21 | Weight | kg
7.4.22 | Tests as per the relevant standards and Employer's Requirements | yes/no | yes
7.5 | 220V DC Batteries
7.5.1 | Applicable standard | - | IEC 60623, IEC 62259, IEC 62485-1, IEC 62485-2
7.5.2 | Manufacturer | -
7.5.3 | Place of manufacture | -
7.5.4 | Type | - | valve-regulated Ni-Cd
7.5.5 | Nominal voltage per cell | V DC
7.5.6 | Number of cells | - | 102
7.5.7 | Nominal voltage of the battery | V DC | 220
7.5.8 | Minimum capacity | Ah | 600
7.5.9 | Capacity corresponding to a discharge time of | h | 10
7.5.10 | Suitable for float and boost charging | yes/no | yes
7.5.11 | Operating lifetime | years | 20
7.5.12 | Installed on corrosion resistant rack | yes/no | yes
7.5.13 | Set of maintenance tools | yes/no | yes
7.5.14 | Dimensions of the battery rack L x W x H | mm
7.5.15 | Weight of the battery | kg
7.5.16 | Accessories as per the Employer's Requirements | yes/no | yes
7.6 | Main 48 V DC Switchgear
7.6.1 | General data
7.6.1.1 | Manufacturer | -
7.6.1.2 | Place of manufacture | -
7.6.1.3 | Model designation | -
7.6.1.4 | Applicable standard | - | IEC 61439, IEC 60947 etc. as per Employer's Requirements
7.6.1.5 | Internal separation outgoing feeders | - | Form 2b
7.6.1.6 | Location of installation | - | indoor
7.6.1.7 | Number of phases | - | L+/L-
7.6.1.8 | Number of busbars | - | 1
7.6.1.9 | Nominal voltage | V DC | 48
7.6.1.10 | Rated power frequency withstand voltage | kV rms | 1.1
7.6.1.11 | Rated short-time current, 3s | kA | 3.3
7.6.1.12 | Rated peak withstand current | kA
7.6.1.13 | Rated current for busbar | A
7.6.1.14 | Power supply for heaters | VAC | 230
7.6.1.15 | Insulation resistance | MΩ | 0.5
7.6.1.16 | Degree of protection | - | IP54
7.6.1.17 | Instruments and accessories in accordance with the Employer's Requirements | yes/no | yes
7.6.2 | Main dimensions
7.6.2.1 | Number of individual panels | -
7.6.2.2 | Dimensions of the individual panels L x W x H | mm
7.6.2.3 | Weight of the individual panels | kg
7.6.3 | Tests
7.6.3.1 | Tests as per the relevant standards and Employer's Requirements | yes/no | yes
7.7 | 48V DC Battery Charger
7.7.1 | Manufacturer | -
7.7.2 | Place of manufacture | -
7.7.3 | Applicable standard | - | IEC 60146
7.7.4 | Location of installation | - | indoor
7.7.5 | Type of controls | - | thyristor control
7.7.6 | Type of cooling | - | self-ventilating
7.7.7 | Rated voltage primary | V | 400
7.7.8 | Rated voltage secondary | V DC | 48±10%
7.7.9 | Rated current | A
7.7.10 | Rated capacity | kVA
7.7.11 | IP protection | IP | 43
7.7.12 | Mounted in metal cabinet | - | yes
7.7.13 | Charging characteristics:
7.7.14 | - Constant voltage range | V
7.7.15 | - Continuous charging voltage per cell and tolerances | V +/-
7.7.16 | - Residual ripple (without connected battery) | % | < 5 % rms
7.7.17 | - Voltage stability with both rectifiers connected to the load | % | +/-1,5
7.7.18 | Noise level | dB (A)
7.7.19 | Blocking diodes in the output circuit of each rectifier | yes/no | yes
7.7.20 | Main dimensions L x W x H | mm
7.7.21 | Weight | kg
7.7.22 | Tests as per the relevant standards and Employer's Requirements | yes/no | yes
7.8 | 48 DC Batteries
7.8.1 | Applicable standard | - | IEC 60623, IEC 62259, IEC 62485-1, IEC 62485-2
7.8.2 | Manufacturer | -
7.8.3 | Place of manufacture | -
7.8.4 | Type | - | valve-regulated Ni-Cd
7.8.5 | Nominal voltage per cell | V DC
7.8.6 | Number of cells | - | 22
7.8.7 | Nominal voltage of the battery | V DC | 48
7.8.8 | Minimum capacity | Ah | 150
7.8.9 | Capacity corresponding to a discharge time of | h | 10
7.8.10 | Suitable for float and boost charging | yes/no | yes
7.8.11 | Operating lifetime | years | 20
7.8.12 | Installed on corrosion resistant rack | yes/no | yes
7.8.13 | Set of maintenance tools | yes/no | yes
7.8.14 | Dimensions of the battery rack L x W x H | mm
7.8.15 | Weight of the battery | kg
7.8.16 | Accessories as per the Employer's Requirements | yes/no | yes
7.9 | AC UPS Inverter
7.9.1 | General data | - | -
7.9.1.1 | Applicable standard | - | IEC 62040
7.9.1.2 | Manufacturer | -
7.9.1.3 | Place of manufacture | -
7.9.1.4 | Type | -
7.9.1.5 | Rated output power at cos phi =0,8 ind | kVA
7.9.1.6 | Rated supply voltage | V DC | 220
7.9.1.7 | Rated output voltage | V AC | 230
7.9.1.8 | Voltage control: | %
7.9.1.9 | - static | % | < +/- 1
7.9.1.10 | - dynamic with 100 % load change | Hz | <5
7.9.1.11 | Frequency | Hz | 50
7.9.1.12 | Frequency stability (mains synchronized) | % | +/- 0,05
7.9.1.13 | Frequency tolerance self synchronized |  | +/- 0,1
7.9.1.14 | Overload capability |  | 125 % - 10 min 150 % - 60 sec
7.9.1.15 | Short circuit capability |  | 300% 3s
7.9.1.16 | Maximum heat loss at rated load | W | -
7.9.1.17 | Acoustic level on 100 % load | dB(A) | < 65 (in 1m)
7.9.1.18 | Efficiency at 100 % load, cos phi 0.8 | % | > 90
7.9.1.19 | Total Harmonic Distortion of Current (THDI):
7.9.1.20 | - linear load | % | <1
7.9.1.21 | - non linear load | % | <5
7.9.1.22 | Static transfer switch | yes / no | yes
7.9.1.23 | Manual bypass switch | yes / no | yes
7.9.1.24 | Network card | yes / no | yes
7.9.1.25 | Interfaces:
7.9.1.26 | RS-232, RJ 45, ModBus | yes / no | yes
7.9.1.27 | Relay cards for operating and fail messages | yes / no | yes
7.9.1.28 | Main dimensions L x W x H | mm
7.9.1.29 | Weight | kg
7.9.1.30 | Tests as per the relevant standards and Employer's Requirements | yes/no | yes
7.10 | Emergency diesel generator
7.10.1 | General
7.10.1.1 | Manufacturer | - | -
7.10.1.2 | Type | - | -
7.10.1.3 | Standard | - | ISO 8528
7.10.1.4 | Performance class | - | G3
7.10.1.5 | Power rating category | - | standby
7.10.1.6 | Single and parallel opertaion with other generating sets and with mains | yes/no | no
7.10.1.7 | Rated output at guarantee site conditions
7.10.1.8 | Lekhnath | kW/kVA | 50/63,5
7.10.1.9 | Damauli | kW | 100/120
7.10.1.10 | Rated speed (max.) | rpm | -
7.10.1.11 | Cooling system | - | water-cooled with closed circuit radiator and fan
7.10.1.12 | Starting mode | - | automatic
7.10.1.13 | Start-up time | sec. | max. 10
7.10.1.14 | Starter | - | battery fed electric starter motor
7.10.1.15 | Type of fuel | - | HSD
7.10.1.16 | Fuel consumption at rated load | - | -
7.10.1.17 | Lekhnath | l/h | -
7.10.1.18 | Damauli | l/h | -
7.10.1.19 | Capacity of fuel oil day tank | - | -
7.10.1.20 | Lekhnath | l | -
7.10.1.21 | Damauli | l | -
7.10.1.22 | Containerised unit | (yes/no) | yes
7.10.1.23 | Sound pressure level (7m) | - | -
7.10.1.17 | Lekhnath | dB(A) | 68
7.10.1.18 | Damauli | dB(A) | 70
7.10.1.24 | Main dimension (HxWxD) | - | -
7.10.1.26 | Lekhnath | mm
7.10.1.27 | Damauli | mm
7.10.1.25 | Weight | - | -
7.10.1.26 | Lekhnath | kg
7.10.1.27 | Damauli | kg
7.10.2 | Generator
7.10.2.1 | Manufacturer | -
7.10.2.2 | Type | -
7.10.2.3 | Standard | - | IEC 60034-22
7.10.2.4 | Apparent power at guarantee site conditions measured at generator terminals
7.10.2.5 | Lekhnath | kVA | 50
7.10.2.6 | Damauli | kVA | 100
7.10.2.7 | Power factor | - | 0.8
7.10.2.8 | Generator cooling system | - | air
7.10.2.9 | Frequency | Hz | 50
7.10.2.10 | Terminals | - | L1, L2, L3 & N
7.10.2.11 | Voltage | V | 400/230
7.10.2.12 | Type of system earthing | - | TN-S
7.10.2.13 | Voltage regulator | - | AVR with a range of ±10%
7.10.2.14 | Protection class of generator | - | min. IP44
7.10.2.15 | Insulation class of generator and exciter | - | F

## 8. C&P System
Technical Data Sheets
BIDDER’S / CONTRACTOR’S GUARANTEED DATA |  | Unit | Data required | Data offered
No. | Description
8. | Control & Protection System
8.1 | General Requirements
8.1.1 | General
8.1.1.1 | Maximum ambient temperature for rated accuracy | °C | IEC 60255-1 –10°C ... +55°C
8.1.1.2 | Maximum storage temperature | °C | IEC 60255-1 -40°C….+70°C
8.1.1.3 | Maximum temp. influence on setting values | %/°C | 0.02
8.1.1.4 | Maximum humidity | % | IEC 60255-1 0-95%
8.1.1.5 | Radiated electromagnetic field | - | IEC 60255-26, Class III
8.1.1.6 | Conducted field disturbance | - | IEC 60255-26 10V 80MHz
8.1.1.7 | Radiated emissions | - | IEC 60255-26 30-1000MHz
8.1.1.8 | Conducted emissions | - | IEC 60255-26 0,15-30 MHz
8.1.1.9 | Insulation tests | - | IEC 60255-27 2 kV 50 Hz, 1 min 2,8 kV DC. 1 min >100M0hm 0,5kV DC
8.1.1.10 | HV Impulse test | - | IEC 60255-27 test voltage 5 kV
8.1.1.11 | Slow damped oscillator wave immunity |  | IEC 60255-26 Level 3
8.1.1.12 | Electrostatic discharge immunity | - | IEC 60255-26 Cl. 3
8.1.1.13 | Fast transients / Burst immunity / Surge immunity | - | IEC 60255-26 Zone A
8.1.1.14 | Power freq. magnetic field test | - | IEC 60255-26 cl. V
8.1.1.15 | Enclosure | - | IEC 60529, IP 50
8.1.1.16 | Mechanical tests (vibration, shock, bump, seismic) | - | IEC 60255-21-1,2,3 Class 1
8.1.2 | Auxiliary Supply
8.1.2.1 | DC supply rated voltage * | V | 220 V DC (+10% ... -20%)
| * Existing Lekhnath Substation | V | 110 V DC (+10% ... -20%)
8.1.2.2 | DC supply ripple | % | 2% ref. value 10% nom. range
8.1.3 | Analogue Input | -
8.1.3.1 | VT phase secondary voltage | V | 110/ √3
8.1.3.2 | Frequency range | Hz | 50 (-5%...+5%)
8.1.3.3 | Frequency dependency of operating value ( each protection function or groups) | %/Hz | <1
8.1.3.4 | Dependency of main protection functions operation from harmonic distortion (2,3,5th, 10% or 20% from fundamental) | % | <5
8.1.3.5 | Voltage withstand
8.1.3.6 | - permanent | x UN | 2
8.1.3.7 | - 10 sec (operative range) | x U N | 4
8.1.3.8 | Secondary current | A | 1
8.1.3.9 | Current withstand (valid for test plugs also)
8.1.3.10 | - permanent | IN | 4
8.1.3.11 | - 1 sec (operative range) | IN | 100
8.1.3.12 | AC burdens
8.1.3.13 | - current circuit | VA(phase | <0,15
8.1.3.14 | - voltage circuit | VA/phase | <0,15
8.1.4 | Binary Inputs
8.1.4.1 | Number | - | 16
8.1.4.2 | Max DC voltage | V
8.1.4.3 | Pulse discrimination | Hz
8.1.5 | Binary Output
8.1.5.1 | For indication or trip | - | IEC 61810-2 min. 16
8.1.5.2 | - max. service voltage | V DC
8.1.5.3 | - max. making current (1s) | A | 10
8.1.5.4 | - continuous current | A | 5
8.1.5.5 | - making current at rated V DC | A | 10
8.1.5.6 | For fast tripping (reed)
8.1.5.7 | - Number | - | 4
8.1.5.8 | - max. service voltage | V DC
8.1.5.9 | - max. making current | A | 0,4 A
8.1.5.10 | - continuous current | A
8.1.5.11 | - making power at rated V DC | W
8.1.5.12 | - breaking power at rated V DC L/R < 40 ms | W
8.1.6 | Cubicles
8.1.6.1 | Protection class | - | IP54
8.1.6.2 | Pre-wired | yes/no | yes
8.1.6.3 | Floor-mounted | yes/no | yes
8.1.6.4 | Steel sheet thickness | mm
8.1.6.5 | Maximum height | mm
8.1.6.6 | Maximum width | mm
8.1.6.7 | Maximum depth | mm
8.1.6.8 | Front-door material | - | glass
8.1.6.9 | Coloring | -
8.1.6.10 | Ventilation | - | forced
8.2 | Transformer Differential Protection - Main 1 and Main 2
8.2.1 | Transformer Differential Protection (87) | -
8.2.1.1 | Manufacturer | - | Bidder to declare
8.2.1.2 | Place of manufacture | - | Bidder to declare
8.2.1.3 | Type / complete designation/ software / firmware version | - | Bidder to declare
8.2.1.4 | Type | - | Biased, dual slope
8.2.1.5 | Ratings
8.2.1.6 | Range of operating coil settings | % of C.T. rating | 1 to 10%
8.2.1.7 | Number of windings | - | 3
8.2.1.8 | Operating time | ms | 20
8.2.1.9 | Range of bias settings | % of C.T. rating | 0,05 to 200
8.2.1.10 | Minimum sensitivity:
8.2.1.11 | - earth faults | % of C.T. rating
8.2.1.12 | - phase faults | % of C.T. rating
8.2.2 | Restricted Earth Fault Protection (87N)
8.2.2.1 | - Type | - | low impedance
8.2.2.2 | - Tripping current range | x IN
8.2.2.3 | - Tripping time range | ms
8.2.2.4 | - Trip criteria | - | 2
8.2.3 | Distance Protection (21)
8.2.3.1 | Number of independent impedance measuring loops | - | 6
8.2.3.2 | Ranges of positive sequence phase reactance setting | Ohm/ph
8.2.3.3 | Ranges of zero sequence reactance setting | Ohm/ph
8.2.3.4 | Ranges of positive sequence phase resistance setting | Ohm/ph
8.2.3.5 | Ranges of zero sequence resistance setting | Ohm/ph
8.2.3.6 | Ranges of timers for all zones | ms | 0-50000
8.2.3.7 | Number of independent impedance zones | - | 4
8.2.3.8 | Type of trip characteristic | - | quadrilateral phase and E/F
8.2.3.9 | - teleprotection features |  | Yes
8.2.3.10 | - type of characteristic of teleprotection | - | PUTT, POTT
8.2.3.11 | - minimum number of auto-reclose cycles (AR-cycles) | - | 3
8.2.3.12 | - fault locator and event (disturbance) recorder | - | Yes
8.2.3.13 | Remote communication
8.2.3.14 | - protocol | - | IEC 61850
8.2.3.15 | - transmission rate | Kbaud | 2048
8.2.3.16 | Selectable trip direction | - | for each zone
8.2.3.17 | Trip mode | - | 1/3- phase
8.2.3.18 | Directional sensitivity | - | unlimited
8.2.3.19 | Phase Current sensitivity | x In | 0,05-0,3
8.2.3.20 | Earth Fault Current sensitivity | x In | 0,05-0,3
8.2.3.21 | Separate adjustment of dead times for 1-ph and multi-phase cycles | yes/no | yes
8.2.3.22 | Setting range of zero sequence compensation factor :
8.2.3.23 | - amplitude | Ohm
8.2.3.24 | - angle | degree
8.2.3.25 | Typical tripping time | ms | 25
8.2.3.26 | Reset time | ms | 30
8.2.3.27 | Typical reset ratio | % | 105
8.2.3.28 | Signaling modes | - | permissive, blocking, intertrip
8.2.3.29 | Load encroachment criteria | - | 2
8.2.4 | Directional Phase Overcurrent (67)
8.2.4.1 | Number of time-current stages | - | 2
8.2.4.2 | Signaling to remote end | - | permissive, blocking for all stages
8.2.4.3 | Current setting range | x IN | 0,1…40
8.2.4.4 | Measuring accuracy | % | 1,5
8.2.4.5 | Reset ratio | -
8.2.4.6 | Directional element:
8.2.4.7 | - measuring angle | degrees | -179…+180
8.2.4.8 | - min operating current | x IN | 0.01
8.2.4.9 | - min operating voltage | x UN | 0.01
8.2.4.10 | - pick-up time | ms | 30
8.2.5 | Overcurrent Protection (50/51, 50N/51N)
8.2.5.1 | Current setting range (from-to) | X IN | 0,10 – 35,00
8.2.5.2 | Measuring accuracy | % | 1,5 % for <10In 5% for >10In
8.2.5.3 | Reset ratio | - | >0,95
8.2.5.4 | Trip characteristics | s | IEC, IEEE, user defined
8.2.5.5 | Start time | ms | 30
8.2.5.6 | Minimum number of DMT stages for 50/51 | - | 2
8.2.5.7 | Minimum number of IDMT stages for 50 | - | 2
8.2.5.8 | Minimum number of DMT stages for 50N/51N | - | 2
8.2.5.9 | Minimum number of IDMT stages for 50N | - | 2
8.2.5.10 | Measurement Mode | - | RMS, peak-to-peak, DFT
8.2.5.11 | Suppression of harmonics | - | RMS, Peak no suppression, DFT < -30dB
8.2.6 | Overexcitation protection (V/Hz)
8.2.6.1 | - Number of stages | - | 2
8.2.6.2 | - Trip characteristics | - | DMT, IDMT, user defined
8.2.6.3 | - Accuracy | % | 1.5
8.2.6.4 | - Start time | ms | 25
8.2.6.5 | - Reset ratio | - | 0.95
8.2.7 | Breaker failure protection (50BF)
8.2.7.1 | Settings
8.2.7.2 | - ranges of current flow monitoring | A | 0,05 – 20,00
8.2.7.3 | - ranges of times | s | 0,00 – 30,00
8.2.8 | Trip Circuit Supervision
8.2.8.1 | - Continuous supervision of complete trip circuit independent of CB position |  | Yes for all trip circuits
8.2.8.2 | - Operation indication and output contacts for remote alarm |  | Yes
8.2.9 | Power swing blocking (for all zones) | yes/no | yes
8.2.10 | Load unbalance protection (46)
8.2.10.1 | Settings
8.2.10.2 | - setting range current stage 1 | A | 0,10 – 35,00
8.2.10.3 | - setting range current stage 2 | A | 0,10 - 35,00
8.2.10.4 | - setting range time delay stage 1 | sec | 0,00 – 30,00
4.2.10.5 | - setting range time delay stage 2 | sec | 0,00 – 30,00
8.2.11 | Overload protection (49)
8.2.11.1 | - k-factor |  | 0,1 – 4,0
8.2.11.2 | - time constant | min | 1,0 – 999,0
8.2.12 | Switch-on to fault | yes/no | yes
8.2.13 | Binary Inputs Transformer protection | yes/no | yes
8.2.14 | Fault Recorder | yes/no | yes
8.2.15 | Measurement Functions | yes/no | yes
8.2.15.1 | 3-ph voltage | yes/no | yes
8.2.15.2 | 3-ph current | yes/no | yes
8.2.15.3 | Residual current | yes/no | yes
8.2.15.4 | Sequence current | yes/no | yes
8.2.15.5 | Sequence voltage | yes/no | yes
8.2.15.6 | 3-ph power | yes/no | yes
8.2.15.7 | Energy monitoring | yes/no | yes
8.3 | Busbar differential protection (87BB) - Main 1 and Main 2
8.3.1 | Busbar differential protection (87BB)
8.3.1.1 | Type | -
8.3.1.2 | Manufacturer | -
8.3.1.3 | Place of manufacture | -
8.3.1.4 | - Centralized/decentralized | - | decentralized or centralized (ref. to scope)
8.3.1.5 | - Type | - | biased low impedance
8.3.1.6 | - Number of zones | - | 4
8.3.1.7 | - Typical operating time | ms | 15
8.3.1.8 | - Accuracy | %pick-up | 5
8.3.1.9 | - Trip criteria | - | min 2
8.3.1.10 | Settings
8.3.1.11 | - ranges of values of restrained protection | I/InO | 0,05 – 2,00
8.3.1.12 | - ranges of values of unrestrained protection | I/InO | 0,5 – 35,00
8.3.1.13 | - ranges of times | sec | 0,00 – 30,00
8.3.1.14 | CT supervision | - | yes
8.3.1.15 | Stub function | - | yes
8.3.1.16 | - Saturation detector | yes/no | yes
8.3.1.17 | - Dead zone protection | yes/no | yes
8.3.1.18 | - Earth fault sensitivity enhancement | yes/no | yes
8.3.1.19 | DC burden | W
8.3.1.20 | AC burden | Ohm
8.3.1.21 | Remote communication
8.3.1.22 | - protocol | - | IEC 61850
8.3.1.23 | - transmission rate | Kbaud | 2048
8.3.2 | Breaker failure protection (50BF)
8.3.2.1 | Settings
8.3.2.2 | - ranges of current flow monitoring | A | 0,05 – 20,00
8.3.2.3 | - ranges of times | s | 0,00 – 30,00
8.3.2.4 | - Number of stages | - | 2
8.3.2.5 | - External trip | yes/no | yes
8.3.2.6 | - Protection trip pulse length | s | 0,05 -2
8.3.4 | End fault Protection (50EF) | yes/no | yes
8.3.5 | Trip Circuit Supervision
8.3.5.1 | - Continuous supervision of complete trip circuit independent of CB position |  | Yes for all trip circuits
8.3.5.2 | - Operation indication and output contacts for remote alarm |  | Yes
8.3.6 | Fault Locator (FL)
8.3.6.1 | Principle | - | impedance based or travelling wave
8.3.6.2 | Measurement in the AR cycle |  | required
8.3.6.3 | Accuracy of measurement for fault currents | (% of line length) | <2,5%
8.4 | Multifunctional Protection Terminal for 220 kV OHL Feeders
8.4.1 | Main 1 - Line Current Differential (87L)
8.4.1.1 | Line Current Differential (87L)
8.4.1.1.1 | Manufacturer | - | Bidder to declare
8.4.1.1.2 | Place of manufacture | - | Bidder to declare
8.4.1.1.3 | Type / complete designation/ software / firmware version | - | Bidder to declare
8.4.1.1.4 | Communication
8.4.1.1.5 | Setting ranges
8.4.1.1.6 | - minimum operating current | x IBASE | 0,1-2,0
8.4.1.1.7 | - slope sections | - | min 2
8.4.1.1.8 | - biased operation | x IBASE | 0,1-10,0
8.4.1.1.9 | - unrestrained operation | x IBASE | 1,0-50,0
8.4.1.1.10 | Second harmonic blocking | - | Required
8.4.1.1.11 | Fifth harmonic blocking | - | Required
8.4.1.1.12 | Operate time (typical) | ms | 20
8.4.1.1.13 | Reset time | ms | 15
8.4.1.1.14 | Critical impulse time | ms | 2
8.4.1.1.15 | Trip mode | - | 1-/3 pole
8.4.1.1.16 | Minimum number of auto-reclose cycles (AR-cycles) | - | 3
8.4.1.1.17 | Fault locator and event (disturbance) recorder | - | Required
8.4.1.1.18 | Remote communication protocol | - | IEC 61850
8.4.1.1.19 | Remote communication transmission rate | Kbaud | 2048
8.4.1.1.20 | Charging current compensation | - | Required
8.4.1.1.21 | Charging current comparison | - | Required
8.4.1.1.22 | Weak end intertrip | - | Required
8.4.1.1.23 | Direct intertrip from binary input | - | Required
8.4.1.1.24 | Time delay | - | IDMT and DT
8.4.1.1.25 | Communication delay compensation | - | describe method
8.4.1.1.26 | In-zone reactor | - | required
8.4.1.2 | Distance Protection (21)
8.4.1.2.1 | Manufacturer | - | Bidder to declare
8.4.1.2.2 | Place of manufacture | - | Bidder to declare
8.4.1.2.3 | Type / complete designation/ software / firmware version | - | Bidder to declare
8.4.1.2.4 | Number of independent impedance measuring loops | - | 6
8.4.1.2.5 | Ranges of positive sequence phase reactance setting | Ohm/ph
8.4.1.2.6 | Ranges of zero sequence reactance setting | Ohm/ph
8.4.1.2.7 | Ranges of positive sequence phase resistance setting | Ohm/ph
8.4.1.2.8 | Ranges of zero sequence resistance setting | Ohm/ph
8.4.1.2.9 | Ranges of timers for all zones | ms | 0-50000
8.4.1.2.10 | Number of independent impedance zones | - | 4
8.4.1.2.11 | Type of trip characteristic | - | quadrilateral phase and E/F
8.4.1.2.12 | - teleprotection features |  | Yes
8.4.1.2.13 | - type of characteristic of teleprotection | - | PUTT, POTT
8.4.1.2.14 | - minimum number of auto-reclose cycles (AR-cycles) | - | 3
8.4.1.2.15 | - fault locator and event (disturbance) recorder | - | Yes
8.4.1.2.16 | Remote communication
8.4.1.2.17 | - protocol | - | IEC 61850
8.4.1.2.18 | - transmission rate | Kbaud | 2048
8.4.1.2.19 | Selectable trip direction | - | for each zone
8.4.1.2.20 | Trip mode | - | 1/3- phase
8.4.1.2.21 | Directional sensitivity | - | unlimited
8.4.1.2.22 | Phase Current sensitivity | x In | 0,05-0,3
8.4.1.2.23 | Earth Fault Current sensitivity | x In | 0,05-0,3
8.4.1.2.24 | Separate adjustment of dead times for 1-ph and multi-phase cycles | yes/no | yes
8.4.1.2.25 | Setting range of zero sequence compensation factor :
8.4.1.2.26 | - amplitude | Ohm
8.4.1.2.27 | - angle | degree
8.4.1.2.28 | Typical tripping time | ms | 25
8.4.1.2.29 | Reset time | ms | 30
8.4.1.2.30 | Typical reset ratio | % | 105
8.4.1.2.31 | Signaling modes | - | permissive, blocking, intertrip
8.4.1.2.32 | Load encroachment criteria | - | 2
8.4.1.2.33 | Power swing blocking (for all zones) | yes/no | yes
8.4.1.2.34 | Switch-on to fault | yes/no | yes
8.4.1.2.35 | Fuse failure blocking | yes/no | yes
8.4.1.2.36 | Out of step tripping | yes/no | yes
8.4.1.3 | Overcurrent Protection (50/51, 50N/51N)
8.4.1.3.1 | Current setting range (from-to) | X IN | 0,10 – 35,00
8.4.1.3.2 | Measuring accuracy | % | 1,5 % for <10In 5% for >10In
8.4.1.3.3 | Reset ratio | - | >0,95
8.4.1.3.4 | Trip characteristics | s | IEC, IEEE, user defined
8.4.1.3.5 | Start time | ms | 30
8.4.1.3.6 | Minimum number of DTL stages for 50/51 | - | 2
8.4.1.3.7 | Minimum number of IDMT stages for 50/51 | - | 2
8.4.1.3.8 | Minimum number of DTL stages for 50N/51N | - | 2
8.4.1.3.9 | Minimum number of IDMT stages for 50N/51N | - | 2
8.4.1.3.10 | Measurement Mode | - | RMS, peak-to-peak, DFT
8.4.1.3.11 | Suppression of harmonics | - | RMS, Peak no suppression, DFT < -30dB
8.4.1.4 | Power swing blocking (for all zones) | yes/no | yes
8.4.1.5 | Directional Earth Fault (67N)
8.4.1.5.1 | Number of time-current stages | - | 2
8.4.1.5.2 | Signaling to remote end | - | permissive, blocking for all stages
8.4.1.5.3 | Current setting range (earth fault) | x IN | 0,1…40
8.4.1.5.4 | Measuring accuracy | %
8.4.1.5.5 | Reset ratio | -
8.4.1.5.6 | Settings
8.4.1.5.7 | - ranges of times | sec | 0,00 – 30,00
8.4.1.5.8 | - ranges of voltage values | V | 0.10 – 120
8.4.1.5.9 | - minimum number of DTL stages for 67 | - | 2
8.4.1.5.10 | - minimum number of IDMT stages for 67 | - | 2
8.4.1.5.11 | - minimum number of DTL stages for 67N | - | 2
8.4.1.5.12 | - minimum number of IDMT stages for 67N | - | 2
8.4.1.5.13 | - teleprotection features | - | Yes
8.4.1.5.14 | - trip mode | - | 1-/3 pole
8.4.1.5.15 | Remote communication protocol | - | IEC 61850
8.4.1.5.16 | Remote communication transmission rate | Kbaud | 2048
8.4.1.5.17 | Directional element:
8.4.1.5.18 | - measuring angle | degrees | -179…+180
8.4.1.5.19 | - min operating current | x IN | 0.01
8.4.1.5.20 | - min operating voltage | x UN | 0.01
8.4.1.5.21 | - pick-up time | ms | <30
8.4.1.6 | Directional Phase Overcurrent (67)
8.4.1.6.1 | Number of time-current stages | - | 2
8.4.1.6.2 | Signaling to remote end | - | permissive, blocking for all stages
8.4.1.6.3 | Current setting range | x IN | 0,1…40
8.4.1.6.4 | Measuring accuracy | %
8.4.1.6.5 | Reset ratio | -
8.4.1.6.6 | Directional element:
8.4.1.6.7 | - measuring angle | degrees | -179…+180
8.4.1.6.8 | - min operating current | x IN | 0.01
8.4.1.6.9 | - min operating voltage | x UN | 0.01
8.4.1.6.10 | - pick-up time | ms | 30
8.4.1.7 | Out of step Protection | yes/no | yes
8.4.1.8 | Load unbalance protection (46)
8.4.1.8.1 | Settings
8.4.1.8.2 | - setting range current stage 1 | A | 0,10 – 35,00
8.4.1.8.3 | - setting range current stage 2 | A | 0,10 - 35,00
8.4.1.8.4 | - setting range time delay stage 1 | sec | 0,00 – 30,00
8.4.1.8.5 | - setting range time delay stage 2 | sec | 0,00 – 30,00
8.4.1.9 | Auto-reclosing (79)
8.4.1.9.1 | Number of shots | - | 3
8.4.1.9.2 | Single -phase cycle | - | 3
8.4.1.9.3 | Three-phase cycle | - | 3
8.4.1.9.4 | Dead time for 3-phase cycle | s
8.4.1.9.5 | Reclaim time | s
8.4.1.9.6 | Type |  | 1-pole, 3-pole or 1-/3-pole
8.4.1.9.7 | Settings
8.4.1.9.8 | - ranges of times | s | 0,01 – 30,00
8.4.1.10 | Synchrocheck (25)
8.4.1.10.1 | Operation modes | - | DLDB, DBDL, Synch, Override
8.4.1.10.2 | Voltage setting | V
8.4.1.10.3 | DU measurement | V | 1…60
8.4.1.10.4 | Dφ measurement | degree | 2…80
8.4.1.11 | Breaker failure protection (50BF)
8.4.1.11.1 | Settings
8.4.1.11.2 | - ranges of current flow monitoring | A | 0,05 – 20,00
8.4.1.11.3 | - ranges of times | s | 0,00 – 30,00
8.4.1.12 | Switch-on to fault | yes/no | yes
8.4.1.13 | Trip Circuit Supervision
8.4.1.13.1 | - Continuous supervision of complete trip circuit independent of CB position |  | Yes for all trip circuits
8.4.1.13.2 | - Operation indication and output contacts for remote alarm |  | Yes
8.4.1.14 | Fault Locator (FL)
8.4.1.14.1 | Measurement Principle | - | impedance based or travelling wave
8.4.1.14.2 | Measurement in the AR cycle |  | required
8.4.1.14.3 | Accuracy of measurement for fault currents | (% of line length) | <2,5%
8.4.1.15 | Measurement Functions
8.4.1.15.1 | 3-ph voltage |  | yes
8.4.1.15.2 | 3-ph current |  | yes
8.4.1.15.3 | Residual current |  | yes
8.4.1.15.4 | Sequence current |  | yes
8.4.1.15.5 | Sequence voltage |  | yes
8.4.1.15.6 | 3-ph power |  | yes
8.4.1.15.7 | Energy monitoring |  | yes
8.4.1.16 | Fault Recorder | yes/no | yes
8.4.2 | Main 2
8.4.2.1 | Distance Protection (21)
8.4.2.1.1 | Manufacturer | - | Bidder to declare
8.4.2.1.2 | Place of manufacture | - | Bidder to declare
8.4.2.1.3 | Type / complete designation/ software / firmware version | - | Bidder to declare
8.4.2.1.4 | Number of independent impedance measuring loops | - | 6
8.4.2.1.5 | Ranges of positive sequence phase reactance setting | Ohm/ph
8.4.2.1.6 | Ranges of zero sequence reactance setting | Ohm/ph
8.4.2.1.7 | Ranges of positive sequence phase resistance setting | Ohm/ph
8.4.2.1.8 | Ranges of zero sequence resistance setting | Ohm/ph
8.4.2.1.9 | Ranges of timers for all zones | s | min 0-50
8.4.2.1.10 | Number of independent impedance zones | - | 4
8.4.2.1.11 | Type of trip characteristic | - | quadrilateral phase and E/F
8.4.2.1.12 | - teleprotection features |  | Yes
8.4.2.1.13 | - type of characteristic of teleprotection | - | PUTT, POTT
8.4.2.1.14 | - minimum number of auto-reclose cycles (AR-cycles) | - | 3
8.4.2.1.15 | - fault locator and event (disturbance) recorder | - | Yes
8.4.2.1.16 | Remote communication
8.4.2.1.17 | - protocol | - | IEC 61850
8.4.2.1.18 | - transmission rate | Kbaud | 2048
8.4.2.1.19 | Selectable trip direction | - | for each zone
8.4.2.1.20 | Trip mode | - | 1/3- phase
8.4.2.1.21 | Directional sensitivity | - | unlimited
8.4.2.1.22 | Phase Current sensitivity | x In | 0,05-0,3
8.4.2.1.23 | Earth Fault Current sensitivity | x In | 0,05-0,3
8.4.2.1.24 | Separate adjustment of dead times for 1-ph and multi-phase cycles | yes/no | yes
8.4.2.1.25 | Setting range of zero sequence compensation factor :
8.4.2.1.26 | - amplitude | Ohm
8.4.2.1.27 | - angle | degree
8.4.2.1.28 | Typical tripping time | ms | 25
8.4.2.1.29 | Reset time | ms | 30
8.4.2.1.30 | Typical reset ratio | % | 105
8.4.2.1.31 | Signaling modes | - | permissive, blocking, intertrip
8.4.2.1.32 | Load encroachment criteria | - | 2
8.4.2.1.33 | Power swing blocking (for all zones) | yes/no | yes
8.4.2.1.34 | Switch-on to fault | yes/no | yes
8.4.2.1.35 | Fuse failure blocking | yes/no | yes
8.4.2.1.36 | Out of step tripping | yes/no | yes
8.4.2.2 | Overcurrent Protection (50/51, 50N/51N)
8.4.2.2.1 | Current setting range (from-to) | X IN | 0,10 – 35,00
8.4.2.2.2 | Measuring accuracy | % | 1,5 % for <10In 5% for >10In
8.4.2.2.3 | Reset ratio | - | >0,95
8.4.2.2.4 | Trip characteristics | s | IEC, IEEE, user defined
8.4.2.2.5 | Start time | ms | 30
8.4.2.2.6 | Minimum number of DTL stages for 50/51 | - | 2
8.4.2.2.7 | Minimum number of IDMT stages for 50/51 | - | 2
8.4.2.2.8 | Minimum number of DTL stages for 50N/51N | - | 2
8.4.2.2.9 | Minimum number of IDMT stages for 50N/51N | - | 2
8.4.2.2.10 | Measurement Mode | - | RMS, peak-to-peak, DFT
8.4.2.2.11 | Suppression of harmonics | - | RMS, Peak no suppression, DFT < -30dB
8.4.2.3 | Directional Earth Fault (67N)
8.4.2.3.1 | Number of time-current stages | - | 2
8.4.2.3.2 | Signaling to remote end | - | permissive, blocking for all stages
8.4.2.3.3 | Current setting range (earth fault) | x IN | 0,1…40
8.4.2.3.4 | Measuring accuracy | %
8.4.2.3.5 | Reset ratio | -
8.4.2.3.6 | Settings
8.4.2.3.7 | - ranges of times | sec | 0,00 – 30,00
8.4.2.3.8 | - ranges of voltage values | V | 0,10 – 120
8.4.2.3.9 | - minimum number of DTL stages for 67 | - | 2
8.4.2.3.10 | - minimum number of IDMT stages for 67 | - | 2
8.4.2.3.11 | - minimum number of DTL stages for 67N | - | 2
8.4.2.3.12 | - minimum number of IDMT stages for 67N | - | 2
8.4.2.3.13 | - teleprotection features | - | Yes
8.4.2.3.14 | - trip mode | - | 1-/3 pole
8.4.2.3.15 | Remote communication protocol | - | IEC 61850
8.4.2.3.16 | Remote communication transmission rate | Kbaud | 2048
8.4.2.3.17 | Directional element:
8.4.2.3.18 | - measuring angle | degrees | -179…+180
8.4.2.3.19 | - min operating current | x IN | 0.01
8.4.2.3.20 | - min operating voltage | x UN | 0.01
8.4.2.3.21 | - pick-up time | ms | <30
8.4.2.4 | Directional Phase Overcurrent (67)
8.4.2.4.1 | Number of time-current stages | - | 2
8.4.2.4.2 | Signaling to remote end | - | permissive, blocking for all stages
8.4.2.4.3 | Current setting range | x IN | 0,1…40
8.4.2.4.4 | Measuring accuracy | %
8.4.2.4.5 | Reset ratio | -
8.4.2.4.6 | Directional element:
8.4.2.4.7 | - measuring angle | degrees | -179…+180
8.4.2.4.8 | - min operating current | x IN | 0.01
8.4.2.4.9 | - min operating voltage | x UN | 0.01
8.4.2.4.10 | - pick-up time | ms | 30
8.4.2.5 | Synchrocheck (25)
8.4.2.5.1 | Operation modes | - | DLDB, DBDL, Synch, Override
8.4.2.5.2 | Voltage setting | V
8.4.2.5.3 | DU measurement | V | 1…60
8.4.2.5.4 | Dφ measurement | degree | 2…80
8.4.2.6 | Breaker failure protection (50BF)
8.4.2.6.1 | Settings
8.4.2.6.2 | - ranges of current flow monitoring | A | 0,05 – 20,00
8.4.2.6.3 | - ranges of times | s | 0,00 – 30,00
8.4.2.7 | Switch-on to fault | yes/no | yes
8.4.2.8 | Trip Circuit Supervision
8.4.2.8.1 | - Continuous supervision of complete trip circuit independent of CB position |  | Yes for all trip circuits
8.4.2.8.2 | - Operation indication and output contacts for remote alarm |  | Yes
8.4.2.9 | Fault Locator (FL)
8.4.2.9.1 | Principle | - | impedance based or travelling wave
8.4.2.9.2 | Measurement in the AR cycle |  | required
8.4.2.9.3 | Accuracy of measurement for fault currents | (% of line length) | <2,5%
8.4.2.10 | Measurement Functions
8.4.2.10.1 | 3-ph voltage |  | yes
8.4.2.10.2 | 3-ph current |  | yes
8.4.2.10.3 | Residual current |  | yes
8.4.2.10.4 | Sequence current |  | yes
8.4.2.10.5 | Sequence voltage |  | yes
8.4.2.10.6 | 3-ph power |  | yes
8.4.2.10.7 | Energy monitoring |  | yes
8.5 | Multifunctional Protection Terminal for 132 kV OHL Feeders
8.5.1 | Distance Protection (21)
8.5.1.1 | Manufacturer | - | Bidder to declare
8.5.1.2 | Place of manufacture | - | Bidder to declare
8.5.1.3 | Type / complete designation/ software / firmware version | - | Bidder to declare
8.5.1.4 | Number of independent impedance measuring loops | - | 6
8.5.1.5 | Ranges of positive sequence phase reactance setting | Ohm/ph
8.5.1.6 | Ranges of zero sequence reactance setting | Ohm/ph
8.5.1.7 | Ranges of positive sequence phase resistance setting | Ohm/ph
8.5.1.8 | Ranges of zero sequence resistance setting | Ohm/ph
8.5.1.9 | Ranges of timers for all zones | s | min 0-50
8.5.1.10 | Number of independent impedance zones | - | 4
8.5.1.11 | Type of trip characteristic | - | quadrilateral phase and E/F
8.5.1.12 | - teleprotection features |  | Yes
8.5.1.13 | - type of characteristic of teleprotection | - | PUTT, POTT
8.5.1.14 | - minimum number of auto-reclose cycles (AR-cycles) | - | 3
8.5.1.15 | - fault locator and event (disturbance) recorder | - | Yes
8.5.1.16 | Remote communication
8.5.1.17 | - protocol | - | IEC 61850
8.5.1.18 | - transmission rate | Kbaud | 2048
8.5.1.19 | Selectable trip direction | - | for each zone
8.5.1.20 | Trip mode | - | 1/3- phase
8.5.1.21 | Directional sensitivity | - | unlimited
8.5.1.22 | Phase Current sensitivity | x In | 0,05-0,3
8.5.1.23 | Earth Fault Current sensitivity | x In | 0,05-0,3
8.5.1.24 | Separate adjustment of dead times for 1-ph and multi-phase cycles | yes/no | yes
8.5.1.25 | Setting range of zero sequence compensation factor :
8.5.1.26 | - amplitude | Ohm
8.5.1.27 | - angle | degree
8.5.1.28 | Typical tripping time | ms | 25
8.5.1.29 | Reset time | ms | 30
8.5.1.30 | Typical reset ratio | % | 105
8.5.1.31 | Signaling modes | - | permissive, blocking, intertrip
8.5.1.32 | Load encroachment criteria | - | 2
8.5.1.33 | Power swing blocking (for all zones) | yes/no | yes
8.5.1.34 | Switch-on to fault | yes/no | yes
8.5.1.35 | Fuse failure blocking | yes/no | yes
8.5.1.36 | Out of step tripping | yes/no | yes
8.5.2 | Overcurrent Protection (50/51, 50N/51N)
8.5.2.1 | Current setting range (from-to) | X IN | 0,10 – 35,00
8.5.2.2 | Measuring accuracy | % | 1,5 % for <10In 5% for >10In
8.5.2.3 | Reset ratio | - | >0,95
8.5.2.4 | Trip characteristics | s | IEC, IEEE, user defined
8.5.2.5 | Start time | ms | 30
8.5.2.6 | Minimum number of DMT stages for 50/51 | - | 2
8.5.2.7 | Minimum number of IDMT stages for 50/51 | - | 2
8.5.2.8 | Minimum number of DMT stages for 50N/51N | - | 2
8.5.2.9 | Minimum number of IDMT stages for 50N/51N | - | 2
8.5.2.10 | Measurement Mode | - | RMS, peak-to-peak, DFT
8.5.2.11 | Suppression of harmonics | - | RMS, Peak no suppression, DFT < -30dB
8.5.3 | Directional Earth Fault (67N)
8.5.3.1 | Number of time-current stages | - | 2
8.5.3.2 | Signaling to remote end | - | permissive, blocking for all stages
8.5.3.3 | Current setting range (earth fault) | x IN | 0,1…40
8.5.3.4 | Measuring accuracy | %
8.5.3.5 | Reset ratio | -
8.5.3.6 | Settings
8.5.3.7 | - ranges of times | sec | 0,00 – 30,00
8.5.3.8 | - ranges of voltage values | V | 0,10 – 120
8.5.3.9 | - minimum number of DTL stages for 67 | - | 2
8.5.3.10 | - minimum number of IDMT stages for 67 | - | 2
8.5.3.11 | - minimum number of DTL stages for 67N | - | 2
8.5.3.12 | - minimum number of IDMT stages for 67N | - | 2
8.5.3.13 | - teleprotection features | - | Yes
8.5.3.14 | - trip mode | - | 1-/3 pole
8.5.3.15 | Remote communication protocol | - | IEC 61850
8.5.3.16 | Remote communication transmission rate | Kbaud | 2048
8.5.3.17 | Directional element:
8.5.3.18 | - measuring angle | degrees | -179…+180
8.5.3.19 | - min operating current | x IN | 0.01
8.5.3.20 | - min operating voltage | x UN | 0.01
8.5.3.21 | - pick-up time | ms | <30
8.5.4 | Directional Phase Overcurrent (67)
8.5.4.1 | Number of time-current stages | - | 2
8.5.4.2 | Signaling to remote end | - | permissive, blocking for all stages
8.5.4.3 | Current setting range | x IN | 0,1…40
8.5.4.4 | Measuring accuracy | %
8.5.4.5 | Reset ratio | -
8.5.4.6 | Directional element:
8.5.4.7 | - measuring angle | degrees | -179…+180
8.5.4.8 | - min operating current | x IN | 0.01
8.5.4.9 | - min operating voltage | x UN | 0.01
8.5.4.10 | - pick-up time | ms | 30
8.5.5 | Out of step Protection | yes/no | yes
8.5.6 | Load unbalance protection (46)
8.5.6.1 | Settings
8.5.6.2 | - setting range current stage 1 | A | 0,10 – 35,00
8.5.6.3 | - setting range current stage 2 | A | 0,10 - 35,00
8.5.6.4 | - setting range time delay stage 1 | sec | 0,00 – 30,00
8.5.6.5 | - setting range time delay stage 2 | sec | 0,00 – 30,00
8.5.7 | Auto-reclosing (79)
8.5.7.1 | Number of shots | - | 2
8.5.7.2 | Single -phase cycle | - | 2
8.5.7.3 | Three-phase cycle | - | 2
8.5.7.4 | Dead time for 3-phase cycle | s
8.5.7.5 | Reclaim time | s
8.5.7.6 | Type |  | 1-pole, 3-pole or 1-/3-pole
8.5.7.7 | Settings
8.5.7.8 | - ranges of times | s | 0,01 – 30,00
8.5.8 | Synchrocheck (25)
8.5.8.1 | Operation modes | - | DLDB, DBDL, Synch, Override
8.5.8.2 | Voltage setting | V
8.5.8.3 | DU measurement | V | 1…60
8.5.8.4 | Dφ measurement | degree | 2…80
8.5.9 | Breaker failure protection (50BF)
8.5.9.1 | Settings
8.5.9.2 | - ranges of current flow monitoring | A | 0,05 – 20,00
8.5.9.3 | - ranges of times | s | 0,00 – 30,00
8.5.10 | Switch-on to fault | yes/no | yes
8.5.11 | Trip Circuit Supervision
8.5.11.1 | - Continuous supervision of complete trip circuit independent of CB position |  | Yes for all trip circuits
8.5.11.2 | - Operation indication and output contacts for remote alarm |  | Yes
8.5.12 | Fault Locator (FL)
8.5.12.1 | Principle | - | impedance based or travelling wave
8.5.12.2 | Measurement in the AR cycle |  | required
8.5.12.3 | Accuracy of measurement for fault currents | (% of line length) | <2,5%
8.5.13 | Measurement Functions
8.5.13.1 | 3-ph voltage |  | yes
8.5.13.2 | 3-ph current |  | yes
8.5.13.3 | Residual current |  | yes
8.5.13.4 | Sequence current |  | yes
8.5.13.5 | Sequence voltage |  | yes
8.5.13.6 | 3-ph power |  | yes
8.5.13.7 | Energy monitoring |  | yes
8.6 | Bay Control Unit
8.6.1.1 | Manufacturer | - | Bidder to declare
8.6.1.2 | Place of manufacture | - | Bidder to declare
8.6.1.3 | Type / complete designation/ software / firmware version | - | Bidder to declare
8.6.1.4 | a) Configurable man-machine interface. |  | Yes for all circuits and auxiliary functions
8.6.1.5 | b) Custom metering and status displays with direct access. |  | Yes
8.6.1.6 | c) Critical information alarms. |  | Yes
8.6.1.7 | d) High accuracy time stamped events recorder |  | Yes
8.6.1.8 | e) Digital fault recording |  | Yes
8.6.1.9 | f) Programmable for indication/control of substation auxiliary devices. |  | Yes
8.6.1.10 | g) IEC 61850 Communication protocol |  | Yes
8.7 | Synchrophasor Measurement Unit
8.7.1.1 | Manufacturer | - | Bidder to declare
8.7.1.2 | Place of manufacture | - | Bidder to declare
8.7.1.3 | Type / complete designation/ software / firmware version | - | Bidder to declare
8.7.1.4 | Standard | - | IEEE C37.118
8.7.1.5 | Message rate | /s | 50
8.7.1.6 | Multicast capability | yes/no | yes

## 9. SCMS
Technical Data Sheets
BIDDER’S / CONTRACTOR’S GUARANTEED DATA |  | Unit | Data required | Data offered
No. | Description
9 | Digital Substation Control & Monitoring System (SCMS)
9.1 | General
9.1.1 | Manufacturer | -
9.1.2 | Type / designation | -
9.1.3 | Availability class according to IEC 60870-4 | - | A3
9.1.4 | System availability | % | >99,95
9.1.5 | MTBF | h | >8760
9.1.6 | Reliability class according to IEC 60870-4 | - | R3
9.1.7 | MTTR | h | <12 h
9.1.8 | Data integrity class | - | I3
9.1.9 | Information error probability | - | IE < 10-14
9.1.10 | Automatic time synchronization at all nodes of the network | yes/no | yes
9.1.11 | Time resolution events | ms | 1
9.1.12 | Fault indication LEDs on modules | yes/no | yes
9.1.13 | Spare function capacity | % | 50
9.1.14 | Spare parts | % | 20
9.2 | Station Bus
9.2.1 | Number of station buses | - | at least two per voltage level
9.2.2 | Protocol | - | IEC 61850-8-1
9.2.3 | Transmission medium | - | fiber
9.2.4 | Transmission rate | MBit/s | min. 100
9.3 | Ethernet Switches
9.3.1 | Number of Ethernet switches | -
9.3.2 | Manufacturer | -
9.3.3 | Type | -
9.3.4 | Power supply:
9.3.5 | - on bay level from station battery | V DC | 220
9.3.6 | - on station level from UPS | V AC | 230
9.4 | Clock System
9.4.1 | Number of clock systems | - | 1
9.4.2 | Manufacturer | -
9.4.3 | Type | -
9.4.4 | Synchronization source | - | GPS
9.4.5 | Synchronization interval | -
9.5 | Station Computer
9.5.1 | Redundant set-up | yes/no | yes
9.5.2 | Manufacturer | -
9.5.3 | Type | -
9.5.4 | Power supply from UPS | V AC | 230
9.6 | Common Bay Unit
9.6.1 | Number of common bay units | - | min. 1 per voltage level
9.6.2 | Manufacturer | -
9.6.3 | Type | -
9.6.4 | Power supply from station battery | V DC | 220
9.7 | Gateways
9.7.1 | Gateways to Remote Control Centers
9.7.1.1 | Manufacturer | - | -
9.7.1.2 | Type/Model | - | -
9.7.1.3 | Number of remote control centers to be interfaced simultaneously | - | ≥2
9.7.1.4 | Serial interface | -
9.7.1.5 | Transmission medium | - | fiber (for IEC 60870-5-104) copper (for IEC 60870-5-101)
9.7.1.6 | Data transmission rate for IEC 61870-5-101 channels | Bit/s | min. 9,6 kBit/s
9.7.1.7 | Data transmission rate for IEC 61870-5-104 channels | Bit/s | min. 64 kBit/s
9.7.1.8 | LAN Interface | -
9.7.1.9 | Transmission medium | -
9.7.1.10 | Minimum data transmission rate | MBit/s | ≥100
9.7.2 | Gateways to interfacing Substation (Existing Lekhnath, future New Damauli 400 kV)
9.7.2.1 | Manufacturer | - | -
9.7.2.2 | Type/Model | - | -
9.7.2.3 | Number of Substations to be interfaced simultaneously | - | 1
9.7.2.4 | Serial interface | -
9.7.2.5 | Transmission medium | - | fiber (for IEC 60870-5-104)
9.7.2.6 | Data transmission rate for IEC 61870-5-104 channels | Bit/s | min. 64 kBit/s
9.7.2.7 | LAN Interface | -
9.7.2.8 | Transmission medium | -
9.7.2.9 | Minimum data transmission rate | MBit/s | ≥100
9.8 | Emergency HMI and maintenance service Computer (notebook/laptop)
9.8.1 | Number | - | 1
9.8.2 | Manufacturer | -
9.8.3 | Type | -
9.8.4 | Hard Disk | GB | >= 160 GB
9.8.5 | Operating System
9.8.6 | Monitor Size | inch
9.9 | Operator Workstations (HMI)
9.9.1 | Number of operator workstations | - | 2
9.9.2 | Manufacturer | -
9.9.3 | Type | -
9.9.4 | Power supply from UPS | V AC | 230
9.9.5 | CPU | -
9.9.6 | Working memory | -
9.9.7 | Hard disk | -
9.9.8 | RAID-System | -
9.9.9 | External memory | -
9.9.10 | Operating system | -
9.9.11 | Monitors per operator stations | - | 2
9.9.12 | Monitor size | inch | 32
9.9.13 | Pixels / Resolution | - | 3840 × 2160 pixels (UHD 4K)
9.9.14 | Desks | - | 2
9.9.15 | Chairs | - | 4
9.10 | MMI-Software
9.10.1 | Manufacturer | -
9.10.2 | Type | -
9.11 | System Performance
9.11.1 | Exchange of display | s | < 1
9.11.2 | Presentation of a binary change in the process display | s | < 0,5
9.11.3 | Presentation of an analogue change in the process display | s | < 1
9.11.4 | From order to process output | s | < 0,5
9.11.5 | From order to updating the display | s | < 1,5
9.12 | Hardcopy Printer
9.12.1 | Number of hardcopy printers | - | 2
9.12.2 | Power supply from UPS | V AC
9.12.3 | Format | DIN | 1 x A3 1 x A4
9.12.4 | Color | yes/no | yes
9.12.5 | Pages / min. | - | 10
9.13 | Service Analysis Software
9.13.1 | Manufacturer | -
9.13.2 | Type | -
9.14 | Control Cubicles
9.14.1 | Pre-wired | yes/no | yes
9.14.2 | Floor-mounted | yes/no | yes
9.14.3 | Steel sheet thickness | mm
9.14.4 | Protection class | - | IP 54
9.14.5 | Maximum height | mm | 2200
9.14.6 | Maximum width | mm | 900
9.14.7 | Maximum depth | mm | 900
9.14.8 | Front-door material | - | glass
9.14.9 | Color | light grey | RAL 7035
9.15 | Weather Station for monitoring main weather parameters: Temperature, Humidity, Lightness (Luminosity, Wind Speed, Wind direction, Rainfall)
9.15.1 | Manufacturer | -
9.15.2 | Type | -
9.15.3 | Standard | - | IEC 61724 for Class A Systems
9.15.4 | Sensors for: | - | -
9.15.5 | Wind direction | - | yes
9.15.6 | Wind speed | - | yes
9.15.7 | Temperature | - | yes
9.15.8 | Telative humidity | - | yes
9.15.9 | Barometric pressure | - | yes
9.15.10 | Solar radiation | - | yes
9.15.11 | Precipitation | - | yes
9.15.12 | communication interface for integration to the SCADA and for remote transmission to the LDC | - | yes
9.14.4 | Protection class outdoor enclosure | - | IP 55 W
8.7.1.6 | Multicast capability | yes/no | yes

## 10. Telecom System
Technical Data Sheets
BIDDER’S / CONTRACTOR’S GUARANTEED DATA |  | Unit | Data required | Data offered
No. | Description
10. | Telecommunication System
10.1 | Fiber optic ducted cable
10.1.1 | Manufacturer | -
10.1.2 | Place of manufacture | -
10.1.3 | Cable designation | -
10.1.4 | Type of cable | - | underground FOC
10.1.5 | Non-metallic cable design/construction | yes/no | yes
10.1.6 | Number of single mode optical fibers per cable | - | 48
10.1.7 | Transmission characteristic as defined in ITU-T G.652D | yes/no | yes
10.1.8 | Loose tube configuration | yes/no | yes
10.1.9 | All dielectric | yes/no | yes
10.1.10 | Rodent protection | yes/no | yes
10.1.11 | Flame retardant | yes/no | yes
10.1.12 | Low smoke zero Halogen | yes/no | yes
10.1.13 | Tensile strength during pulling | N | 3000
10.1.14 | Tensile strength during operation | N | 1500
10.1.15 | Operation temperature range | °C | -20 to +70
10.1.16 | Peripheral strength members | - | glass yarns
10.1.17 | Fibers
10.1.18 | Type | - | single mode
10.1.19 | Fiber characteristics according to | - | ITU.T G.652D
10.1.20 | Main transmission wavelengths | nm | 1310, 1550
10.1.21 | Cut-off wave length lcc | nm | ≤ 1260
10.1.22 | Mode field diameter | µm | 8,8 – 9,6 µm @ 1310 nm, 9,9 – 10,9 µm @ 1550 nm
10.1.23 | Optical cladding diameter | µm | 125 ± 0,7
10.1.24 | Concentricity error | µm | ≤ 0,5
10.1.25 | Cladding non-circularity | % | ≤ 1
10.1.26 | Maximum attenuation @ 1550 nm | dB/km | ≤ 0,21
10.1.27 | Maximum attenuation @ 1310 nm | dB/km | ≤ 0,34
10.1.28 | Bending test, additional loss, 1 turn on 32 mm mandrel, @ 1550 n | dB | 0.03
10.1.29 | Bending test, additional loss, 100 turns on 60mm mandrel, @ 1550 nm | dB | 0.03
10.1.30 | Maximum chromatic dispersion @ 1550 nm | ps/(nm.km) | ≤ 18
10.1.31 | Maximum chromatic dispersion @ 1310 nm | ps/(nm.km) | ≤ 3,5
10.1.32 | Maximum Polarisation Mode Dispersion (PMD) per individual fiber | ps/√km | 0.1
10.2 | Pigtails
10.2.1 | Manufacturer | -
10.2.2 | Designation | -
10.2.3 | Fiber type | - | Single mode ITU-T G.652D
10.2.4 | Connector type | - | FC/UPC
10.2.5 | Insertion loss | dB | ≤ 0,2
10.2.6 | Return loss | dB | ≥ 50
10.2.7 | Minimum length | m | 1
10.2.8 | Diameter | mm
10.2.9 | Halogen free | yes/no | yes
10.2.10 | Mechanical and thermal certification in accordance with Telcordia GR-326-Core | yes/no | yes
10.2.11 | Maximum Polarisation Mode Dispersion (PMD) per individual fiber | ps/√km | 0.1
10.2.12 | Operation temperature range | °C | -20 to +70
10.3 | Fiber optic patch-cords
10.3.1 | Manufacturer | -
10.3.2 | Designation | -
10.3.3 | Applicable standards/recommendations | - | IEC 60189-1, IEC 60304, ITU-T G.652D
10.3.4 | Fiber type | - | Single mode ITU-T G.652D
10.3.5 | Connector / plug type | - | FC/UPC
10.3.6 | Insertion loss | dB | ≤ 0,2
10.3.7 | Return loss | dB | ≥ 50
10.3.8 | Minimum length | m | 1
10.3.9 | Diameter | mm
10.3.10 | Minimum boot length (measured from ferrule’s end) | mm | ≥ 49
10.3.11 | Nominal thickness of the sheath | mm | ≥ 1,4
10.3.12 | Tensile strength | N | ≥ 100
10.3.13 | Minimum allowed bending radius | mm | ≤ 30
10.3.14 | Halogen free | yes/no | yes
10.3.15 | Mechanical and thermal certification in accordance with Telcordia GR-326-Core | yes/no | yes
10.3.16 | Maximum Polarisation Mode Dispersion (PMD) per individual fiber | ps/√km | 0.1
10.3.17 | Refractive index of the optical fibers @ λ = 1550 nm and @ λ = 1625 nm | -
10.3.18 | Operation temperature range | °C | -20 to +70
10.4 | Patch Panels
10.4.1 | Manufacturer | -
10.4.2 | Place of manufacture | -
10.4.3 | Designation | -
10.4.4 | Type | - | Sliding type
10.4.5 | Material | - | anodized aluminum
10.4.6 | Height | - | 2U
10.4.7 | Minimum number of SC adapter per panel | -
10.4.8 | Connector / plug type (min. two (2) per panel) | - | FC/UPC
10.5 | Hybrid technology SDH and MPLS - TP equipment
10.5.1 | Multiplexer Manufacturer | -
10.5.2 | Multiplexer type | -
10.5.3 | Access Multiplexer Manufacturer | -
10.5.4 | Acess Multiplexer type | -
10.5.5 | Terminal equipment Manufacturer | -
10.5.6 | Teleprotection equipment manufacturer | -
10.5.7 | Teleprotection equipment type | - | TEBIT
10.5.8 | Maximum extension of transmission capacity of individual terminal by adding plug-in cards | - | 60%
10.5.9 | Ditto for multiplexer based on 2 Mbit-hierarchy | - | 60%
10.5.10 | Maximum extension for multiplexer and terminal equipment racks | - | 60%
10.5.11 | Protection class(es) of terminal equipment racks | - | 50%
10.5.12 | Operating range of fiber optic terminals, depending of the site | MBit/s | STM-4 and 10G for MPLS – TP
10.5.13 | Operating principle of optical transmitter | -
10.5.14 | Nominal operating wavelength | nm | 1550
10.5.15 | Remaining overall system margin at start of life/end of life | -
10.5.16 | Receiver sensitivity (@ BER of 10-10) at start of life/end of life | BER
10.5.17 | Bit error rate (path including terminals) at:
10.5.18 | - n x 2 MBit/s | BER
10.5.19 | - Jitter performance | - | B1: ≤ 1,5 B2: ≤ 0,2
10.5.20 | - n x 2 MBit/s | -
10.5.21 | - Accuracy of internal clock | ppm | ± 4,6
10.5.22 | - Line code (optical) | - | NRZ
10.5.23 | - Line code (electrical) | - | HDB2 or AMI
10.6 | IP-PBX
10.6.1 | Manufacturer | -
10.6.2 | Place of manufacture | -
10.6.3 | Designation | -
10.6.4 | Number of subscribers | - | ≥ 300
10.6.5 | Integrated VoIP functionalities | yes/no | yes
10.6.6 | Integrable into Customer's existing telephony system as well as into the existing telecommunication system | yes/no | yes
10.7 | Telecommunication Cubicles
10.7.1 | Manufacturer | -
10.7.2 | Type | - | free standing, anchoring to floor
10.7.3 | Steel sheet thickness | mm
10.7.4 | Protection class | - | IP 54
10.7.5 | Maximum width | mm | 800
10.7.6 | Maximum height | mm | 2200
10.7.7 | Maximum depth | mm | 800
10.7.8 | Color | light grey | RAL 000 70 00

## 11. Cables
Technical Data Sheets
BIDDER’S / CONTRACTOR’S GUARANTEED DATA |  | Unit | Data required | Data offered
No. | Description
11. | Cable Systems
11.1 | 132 kV Cable System
11.1.1 | General
11.1.1.1 | Highest voltage for equipment | kV | 145
11.1.1.2 | Rated frequency | Hz | 50
11.1.1.3 | Nominal voltage | kV | 132
11.1.1.4 | Rated lightning impulse withstand voltage | kV, peak | 650
11.1.1.5 | Rated power frequency withstand voltage | kV, r.m.s. | 190
11.1.1.6 | System neutral | - | Solidly earthed
11.1.1.7 | System highest 3-phase short-circuit current level (1 s) | kA | 23
11.1.1.8 | System highest single-phase short-circuit current level (1 s) | kA | 23
11.1.2 | Main Design Parameters
11.1.2.1 | Max. ambient temperature | °C | 50
11.1.2.2 | Max. thermal resistivity of the pre-cast concrete | K.m/W | 1
11.1.3 | 132 kV cables
11.1.3.1 | General
11.1.3.1.1 | Voltage designation (Uo/U/Um) | kV | 76/132/145
11.1.3.1.2 | Conductor details:
11.1.3.1.3 | Minimum cross section | mm2 | 300
11.1.3.1.4 | Material | - | Copper
11.1.3.1.5 | Construction | - | Circular stranded Class 2-compacted (IEC 60228)
11.1.3.1.6 | Water blocking mechanism | - | swelling tapes and yarns
11.1.3.2 | Conductor screen
11.1.3.2.1 | Material | - | Extruded semi-conductive compound cross-linked (super smooth)
11.1.3.2.2 | Nominal thickness | mm | 1,2
11.1.3.2.3 | Minimum thickness | mm | 0.8
11.1.3.2.4 | Maximum allowed protrusion into insulation | mm | 0.06
11.1.3.2.5 | Maximum electric stress over conductor screen (at Uo) | kV/mm | 7,8
11.1.3.3 | Insulation
11.1.3.3.1 | Material | - | Cross-Linked Polyethylene (XLPE)
11.1.3.3.2 | Nominal thickness | mm | 17
11.1.3.3.3 | Minimum thickness | mm | 15,3
11.1.3.4 | Insulation screen
11.1.3.4.1 | Material | - | Extruded semi-conductive compound cross-linked (super smooth)
11.1.3.4.2 | Nominal thickness | mm | 1,2
11.1.3.4.3 | Minimum thickness | mm | 0,8
11.1.3.4.4 | Maximum electric stress over insulation screen (at Uo) | kV/mm | 3,4
11.1.3.5 | Extrusion process
11.1.3.5.1 | Type |  | Simultaneous triple extrusion
11.1.3.5.2 | Curing environment |  | Dry Nitrogen
11.1.3.5.3 | Curing temperature/pressure | °C/Bar | 210-250/10
11.1.3.5.4 | Cooling environment | - | Dry Nitrogen
11.1.3.5.5 | Cooling pressure | Bar | 10
11.1.3.6 | Degassing
11.1.3.6.1 | Temperature/duration | °C/days
11.1.3.7 | Maximum tangent of dielectric loss angle |  | 0.0005
11.1.3.8 | Bedding/longitudinal water blocking mechanism
11.1.3.8.1 | Material | - | semi-conductive water swelling tapes
11.1.3.8.2 | Number of tapes | # | 2 (50% overlap)
11.1.3.8.3 | Approximate thickness of the tapes | mm | 0.56
11.1.3.9 | Metallic screen/sheath
11.1.3.9.1 | Material | - | Copper wires
11.1.3.9.2 | Minimum copper wire screen cross-section | mm2 | 85
11.1.3.9.3 | Indicative number of wires x wire diameter | # x mm | 72 x 1,23
11.1.3.9.4 | Material of equalizing tapes | - | Copper
11.1.3.9.5 | Number and cross-section of equalizing tapes |  | 1 x 1mm2
11.1.3.10 | Radial water blocking mechanism
11.1.3.10.1 | Material |  | Aluminum tape with co-polymer
11.1.3.10.2 | Application method |  | welded or overlapped and glued
11.1.3.10.3 | Tape thickness: aluminum/PE | mm | 0,2/0,06
11.1.3.10.4 | For overlapped tapes: overlap strength |  | > 0,5 N/mm
11.1.3.11 | Outer sheath
11.1.3.11.1 | Material |  | High Density Polyethylene (ST7)
11.1.3.11.2 | Nominal thickness | mm | 4
11.1.3.11.3 | Thickness of the extruded outer semi-conductive layer | mm
11.1.3.11.4 | Outer diameter | mm
11.1.3.12 | Other characteristics
11.1.3.12.1 | Cable weight | kg/m
11.1.3.12.2 | Maximum DC resistance of conductor at 20°C | OHM/km | 0.1
11.1.3.12.3 | Maximum AC resistance of conductor at 90°C | OHM/km
11.1.3.12.4 | Maximum DC resistance of metallic screen at 20°C | OHM/km | 0.22
11.1.3.12.5 | Maximum capacitance | pF/m
11.1.3.12.6 | Minimum full load permanent (100%) operation electric current rating | A | 331
11.1.3.12.7 | Minimum short-circuit current capacity for the copper wire screen assuming that the conductor start temperature is 90°C and a final temperature of 250°C (during 1 s) | kA | 12
11.1.4 | Cable trough
11.1.4.1 | Material | - | Pre-Cast Concrete
11.1.4.2 | Minimum traffic load requirement (DIN 1072) | - | SLW 60
11.1.4.3 | Maximum length of the pre-cast elements | m | 6
11.1.4.4 | Maximum width of the cover slab | m | 1
11.1.4.5 | Provisions for lifting the cover slab | - | Yes
11.1.4.6 | Minimum thickness of the concrete | mm | 150
11.1.5 | Outdoor Terminations
11.1.5.1 | Type | - | Outdoor Prefabricated, insulating filling compound, composite insulator
11.1.5.2 | Voltage designation (Uo/U (Um) | - | 76/132/145
11.1.5.3 | Pollution class | - | IEC 60815/IV (43 mm/kV)
11.1.5.4 | Conductor connection - minimum cross-section | mm2 | 300
11.1.5.5 | Top bolt connection | - | shear bolt
11.1.5.6 | Base plate | - | Aluminum
11.1.5.7 | Number of post insulators | # | 4
11.1.5.8 | Type of post insulators | - | epoxy resin
11.1.5.9 | Dielectric strength of the post insulators | kV/mm | 20
11.1.5.10 | Lightning impulse voltage test | kV | 650
11.1.5.11 | Power frequency AC voltage test (30 minutes) | kV | 190
11.1.5.12 | Maximum partial discharge test at 1.5 x U0 | pC | 5
11.1.5.13 | Minimum electric current rating | - | exceeding the minimum electric current rating of the 132 kV cable
11.1.5.14 | Minimum single phase Short-circuit current capacity for assuming that the conductor start temperature is 90°C and a final temperature of 250°C (during 1 s) | kA | 12
11.1.5.15 | All stress control elements PD routine tested | yes/no | Yes
11.1.6 | Clamps for connection to the outdoor terminations top-bolt
11.1.6.1 | Voltage level | kV | 132
11.1.6.2 | Type | - | Bolted straight or 90°
11.1.6.3 | Cross-section | - | Suitable to withstand without any mechanical or electrical degradation the cable maximum electric current rating and 3-phase short-circuit current
11.1.7 | GIS terminations
11.1.7.1 | Maximum operating voltage (Um) | kV | 145
11.1.7.2 | Conductor connection - minimum cross-section | mm2 | 300
11.1.7.3 | Lightning impulse voltage | kV | 650
11.1.7.4 | Power frequency AC voltage test (1 minute) | kV | 275
11.1.7.5 | Maximum partial discharge level at 2 x U0 | pC | 2
11.1.7.6 | Minimum electric current rating | - | exceeding the minimum electric current rating of the 132 kV cable
11.1.7.7 | Minimum single phase Short-circuit current capacity for assuming that the conductor start temperature is 90°C and a final temperature of 250°C (during 1 s) | kA | exceeding the minimum short-circuit rating of the 132 kV cable
11.1.7.8 | All stress control elements PD routine tested | yes/no | Yes
11.1.8 | Link Boxes
11.1.8.1 | Outer box | - | Stainless steel
11.1.8.2 | Earthing links | - | copper with suitable cross section for the foreseeable short-circuit currents
11.1.8.3 | Minimum protection class for the buried boxes | - | IP 68
11.1.8.4 | Minimum protection class for the gantry mounted boxes | - | IP 66
11.1.8.5 | Short circuit typed test | yes/no | yes
11.1.8.6 | Water ingression typed test | yes/no | yes
11.1.9 | Lead bond cables
11.1.9.1 | Voltage level (Uo/U) | kV | 0,6/1
11.1.9.2 | Single core minimum copper cross section | mm2 | 95
11.1.9.3 | Coaxial minimum copper cross section | mm2 | 2 x 95
11.1.9.4 | Insulation | - | XLPE
11.1.9.5 | Outer sheath | - | PVC (ST2)
11.1.10 | Parallel earth cables
11.1.10.1 | Voltage level (Uo/U) | kV | 0,6/1
11.1.10.2 | Minimum copper cross section | mm2 | 95
11.1.10.3 | Insulation | - | XLPE
11.1.10.4 | Outer sheath | - | PVC (ST2)
11.1.11 | Cable cleats/clamps
11.1.11.1 | Type | - | Single core
11.1.11.2 | Material | - | UV resistant Polymer liner with stainless steel cleat
or UV resistant Polymer reinforced with glass fiber liner and stainless steel bolts and nuts
stand
or aluminum with adjustable rod
11.1.11.3 | Stainless steel quality | - | 316 L
11.1.11.4 | Mechanical strength - withstand a short circuit current of 23 kA without deformation and maintaining the cable firmly fixed to the attachment point | yes/no | Yes
11.1.11.5 | Fire resistance - compliant with VDE 0304 Part 3 Class IIA | yes/no | Yes
11.1.11.6 | Operation temperature | °C | From 0 to +120
11.1.11.7 | Cable diameter range | - | Suitable for the 132 kV cable outer diameter
11.1.12 | Support structures for the outdoor terminations
11.1.12.1 | Material | - | Hot-dip galvanized steel
11.1.12.2 | Minimum zinc thickness | mm | 75
11.1.12.3 | Foundation - concrete class | - | C25/30 as per BS EN 206-1
11.1.12.4 | Foundation - Minimum quality standard for the steel reinforcement | - | B400SD
EN 10080
11.1.13 | 132 kV cable pulling
11.1.13.1 | Maximum permissible pulling force on conductors | N/mm2 | 50 N/mm2 - Al conductors
60 N/mm2 - Cu conductors
11.1.13.2 | Maximum side wall pressure - inside PVC or PE ducts (for road crossings - if any) | N/m | 7000
| Maximum side wall pressure - contact with rollers | N | 700
| Minimum bending radius of the PVC or PE ducts (for road crossings - if any) | m | 4
11.1.13.3 | Minimum bending radius for the cables | - | 20 x Cable outer diameter
11.1.13.4 | Lubricant to reduce friction during the cable pulling through the ducts | - | Chemically neutral, biodegradable and compatible with the cable outer sheath
11.1.13.5 | Cable installation temperature range | °C | +5°C to +35°C
11.1.14 | Post-installation tests
11.1.14.1 | Sheath DC test for all cable single lengths immediately before the assembly of joints or sealing ends | - | 10 kV during 1 minute
11.1.14.2 | Confirmation of the phase sequence | yes/no | Yes
11.1.14.3 | Measurement of the line impedance | yes/no | Yes
11.1.14.4 | Measurement of the capacitance | yes/no | Yes
11.1.14.5 | AC voltage test with resonant equipment | - | 132 kV during 1 hour
11.1.14.6 | PD level for joints and sealing ends with resonant equipment | - | For 96 kV no PD over the background noise level
11.2 | 33 kV Cable Systems
11.2.1 | 33 kV power cable (Main connections)
11.2.1.1 | Manufacturer | -
11.2.1.2 | Place of manufacture | -
11.2.1.3 | Type | - | single-core
11.2.1.4 | Waterproof armor
| · single core |  | AWA
11.2.1.5 | Insulation material | - | XLPE
11.2.1.6 | Conductor material | - | copper
11.2.1.7 | Applicable standard | - | IEC 60502‑2
11.2.1.8 | Screen material | - | copper
11.2.1.9 | Minimum cable voltage rating U0/U(Um) | kV | 18/30(36)
11.2.1.10 | Rated frequency | Hz | 50
11.2.1.11 | Cross Section | mm2 | ≥300
11.2.1.12 | Minimum bending radius (single core cables) | mm | 15 x d
11.2.1.13 | Rated short circuit current (1 s): | kA
| · conductor |  | 10
| · screen, min. |  | 10
11.2.1.14 | Maximum conductor temperature normal operation | °C | 90
11.2.1.15 | Maximum conductor temperature after short circuit | °C | 250
11.2.1.16 | Rated current | A | 630 A
11.2.1.17 | Nominal thickness of insulation at rated voltage | mm
11.2.1.18 | Weight | kg/m
11.2.1 | 33 kV power cable (aux. Transformers 630 kVA)
11.2.1.1 | Manufacturer | -
11.2.1.2 | Place of manufacture | -
11.2.1.3 | Type | - | single-core
11.2.1.4 | Waterproof armor
| · single core |  | AWA
11.2.1.5 | Insulation material | - | XLPE
11.2.1.6 | Conductor material | - | copper
11.2.1.7 | Applicable standard | - | IEC 60502‑2
11.2.1.8 | Screen material | - | copper
11.2.1.9 | Minimum cable voltage rating U0/U(Um) | kV | 18/30(36)
11.2.1.10 | Rated frequency | Hz | 50
11.2.1.11 | Cross Section | mm2 | ≥120
11.2.1.12 | Minimum bending radius (single core cables) | mm | 15 x d
11.2.1.13 | Rated short circuit current (1 s): | kA
| · conductor |  | 10
| · screen, min. |  | 10
11.2.1.14 | Maximum conductor temperature normal operation | °C | 90
11.2.1.15 | Maximum conductor temperature after short circuit | °C | 250
11.2.1.16 | Rated current | A
11.2.1.17 | Nominal thickness of insulation at rated voltage | mm
11.2.1.18 | Weight | kg/m
11.2.2 | Accessories 33 kV cable
11.2.2.1 | Cable termination | -
11.2.2.2 | Applicable standard | - | IEC 60502-2
11.2.2.3 | Type | -
11.2.2.4 | Insulation material | -
11.2.2.5 | Conductor connection | -
11.2.3 | Tests as per the relevant standards and Employer's Requirements | yes/no | yes
11.3 | 11 kV Cable Systems
11.3.1 | 11 kV single core power cable (8 MVA Transformer - SWG)
11.3.1.1 | Manufacturer | -
11.3.1.2 | Place of manufacture | -
11.3.1.3 | Type | - | single-core
11.3.1.4 | Waterproof armor
| · single core |  | AWA
11.3.1.5 | Insulation material | - | XLPE
11.3.1.6 | Conductor material | - | copper
11.3.1.7 | Applicable standard | - | IEC 60502‑2
11.3.1.8 | Screen material | - | copper
11.3.1.9 | Minimum cable voltage rating U0/U(Um) | kV | 6/10(12)
11.3.1.10 | Rated frequency | Hz | 50
11.3.1.11 | Cross Section | mm2 | ≥300
11.3.1.12 | Minimum bending radius (single core cables) | mm | 15 x d
11.3.1.13 | Rated short circuit current (1 s): | kA
| · conductor |  | 10
| · screen, min. |  | 10
11.3.1.14 | Maximum conductor temperature normal operation | °C | 90
11.3.1.15 | Maximum conductor temperature after short circuit | °C | 250
11.3.1.16 | Rated current | A | 505
11.3.1.17 | Nominal thickness of insulation at rated voltage | mm
11.3.1.18 | Weight | kg/m
11.3 | 11 kV Cable Systems
11.3.1 | 11 kV single core power cable (outgoing feeders)
11.3.1.1 | Manufacturer | -
11.3.1.2 | Place of manufacture | -
11.3.1.3 | Type | - | single-core
11.3.1.4 | Waterproof armor
| · single core |  | AWA
11.3.1.5 | Insulation material | - | XLPE
11.3.1.6 | Conductor material | - | copper
11.3.1.7 | Applicable standard | - | IEC 60502‑2
11.3.1.8 | Screen material | - | copper
11.3.1.9 | Minimum cable voltage rating U0/U(Um) | kV | 6/10(12)
11.3.1.10 | Rated frequency | Hz | 50
11.3.1.11 | Cross Section | mm2 | ≥120
11.3.1.12 | Minimum bending radius (single core cables) | mm | 15 x d
11.3.1.13 | Rated short circuit current (1 s): | kA
| · conductor |  | 10
| · screen, min. |  | 10
11.3.1.14 | Maximum conductor temperature normal operation | °C | 90
11.3.1.15 | Maximum conductor temperature after short circuit | °C | 250
11.3.1.16 | Rated current | A
11.3.1.17 | Nominal thickness of insulation at rated voltage | mm
11.3.1.18 | Weight | kg/m
11.3.3 | Accessories 11 kV cable
11.3.3.1 | Cable termination | -
11.3.3.2 | Applicable standard | - | IEC 60502-2
11.3.3.3 | Type | -
11.3.3.4 | Insulation material | -
11.3.3.5 | Conductor connection | -
11.3.4 | Tests as per the relevant standards and Employer's Requirements | yes/no | yes
11.4 | LV Power Cables
11.4.1 | LV Power cables single-core
11.4.1.1 | Applied standard | - | IEC 60502-1
11.4.1.2 | Manufacturer | -
11.4.1.3 | Place of manufacture | -
11.4.1.4 | Fire performance | - | flame retardant LSZH
11.4.1.5 | Insulation material | -
11.4.1.6 | Rated voltage Uo/U | kV | 0,6/1
11.4.1.7 | Highest voltage | kV | 1.2
11.4.1.8 | Category of cable | - | A
11.4.1.9 | Maximum conductor temperature normal operation | °C
11.4.1.10 | Maximum conductor temperature after short circuit | °C
11.4.1.11 | Conductor material | - | copper
11.4.1.12 | Nominal thickness of insulation at rated voltage | mm
11.4.1.13 | Weight | kg/m
11.4.1.14 | Tests as per the relevant standards and Employer's Requirements | yes/no | yes
11.4.2 | LV power cables three- & five- core
11.4.2.1 | Applied standard | IEC | 60502-1
11.4.2.2 | Manufacturer | -
11.4.2.3 | Place of manufacture | -
11.4.2.4 | Fire performance | - | flame retardant LSZH
11.4.2.5 | Insulation material | - | PVC
11.4.2.6 | Rated voltage Uo/U | kV | 0,6/1
11.4.2.7 | Highest voltage | kV | 1.2
11.4.2.8 | Category of cable | - | A
11.4.2.9 | Maximum conductor temperature normal operation | °C
11.4.2.10 | Maximum conductor temperature after short circuit | °C
11.4.2.11 | Conductor material | - | copper
11.4.2.12 | Nominal thickness of insulation at rated voltage | mm
11.4.2.13 | Weight | kg/m
11.4.2.14 | Tests as per the relevant standards and Employer's Requirements | yes/no | yes
11.4.3 | Control & DC Cables
11.4.3.1 | Applied standard | IEC | 60502-1
11.4.3.2 | Manufacturer | -
11.4.3.3 | Place of manufacture | -
11.4.3.4 | Fire performance | - | flame retardant LSZH
11.4.3.5 | Insulation material | -
11.4.3.6 | Rated voltage Uo/U | kV | 0,6/1
11.4.3.7 | Highest voltage | kV | 1.2
11.4.3.8 | Category of cable | - | B
11.4.3.9 | Maximum conductor temperature normal operation | °C
11.4.3.10 | Maximum conductor temperature after short circuit | °C
11.4.3.11 | Conductor material | - | copper
11.4.3.12 | Nominal thickness of insulation at rated voltage | mm
11.4.3.13 | Tests as per the relevant standards and Employer's Requirements | yes/no | yes
11.4.4 | Cable Trays
11.4.4.1 | Applicable standard | - | IEC 61537
11.4.4.2 | Manufacturer | -
11.4.4.3 | Place of manufacture | -
11.4.4.4 | Material | - | steel
11.4.4.5 | Corrosion protection | - | Hot dip galvanization
11.4.4.6 | Thickness of galvanization | µm | ≥100
11.4.4.7 | Tests as per the relevant standards and Employer's Requirements | yes/no | yes

## 12. Earthing & Lightning Prot.
Technical Data Sheets
BIDDER’S / CONTRACTOR’S GUARANTEED DATA |  | Unit | Data required | Data offered
No. | Description
12. | Earthing & Lightning Protection System
12.1 | Earthing System
12.1.1 | Manufacturer | -
12.1.2 | Applicable standards | - | IEC 60364, IEC 60479, IEC 60621, IEC 61936‑1, IEC 62305, IEEE 80
12.1.3 | Calculation of the length of the earthing mesh conductor according to | - | IEEE 80
12.1.4 | Calculation of step voltage according to | - | IEEE 80
12.1.5 | Calculation of touch voltages according to | - | IEEE 80
12.1.6 | Material for grid | - | stranded copper conductor
12.1.7 | Minimum cross section of the grid conductor | mm2 | ≥150
12.1.8 | Material for rods | - | copper clad round steel
12.1.9 | Diameter of rods | mm | 16
8.1.10 | Connection method of conductor in the ground | - | exothermic weld
8.1.11 | Material for fixing the earthing conductor clamps | - | by compression
8.1.12 | Clamp material for earthing conductor connections to rods | - | bronze
8.1.13 | Material for bolts and nuts | - | galvanized steel
8.1.14 | Method of connection, earthing conductor to steel structure | - | bolts, nut, washers and lock washers
8.1.15 | Minimum depth of burial | m | 0.8
8.1.16 | Earthing resistance of the complete substation | Ω | ≤0.5
12.2 | Lightning Protection System
12.2.1 | Applied standard | - | IEC 62305 NFPA 780
12.2.2 | Manufacturer | -
12.2.3 | Design | - | Rolling sphere principle
12.2.4 | Material | - | Copper tape with finials on buildings and overhead conductor for switchyard
12.2.5 | Cross section | mm2 | ≥120
12.3 | Tests
12.3.1 | Tests according to relevant standards and Employer's Requirements | yes/no | yes

## 13. Lighting & Small Power
Technical Data Sheets
BIDDER’S / CONTRACTOR’S GUARANTEED DATA |  | Unit | Data required | Data offered
No. | Description
13. | Lighting & Small Power System
13.1 | Lighting Installation
13.1.1 | General
13.1.1.1 | Applicable standards | - | IEC 62717 IEC 62722 IEC 60061 IEC 60364 IEC 60598 IEC 61347 IEC 62444 IEC 62560 IEC 63220 IEC 63221 ISO 30061 EN 50171
13.1.1.2 | Rated voltage | V AC | 230/400
13.1.1.3 | Frequency | Hz | 50
13.1.1.4 | Lighting Type | - | LED
13.1.2 | Lighting Fixtures
13.1.2.1 | Manufacturer | - | -
13.1.2.2 | Type: | - | -
13.1.2.3 | Indoor lighting technical rooms | - | -
13.1.2.4 | Indoor lighting high bay | - | -
13.1.2.5 | Indoor lighting offices | - | -
13.1.2.6 | Indoor lighting control room | - | -
13.1.2.7 | Indoor lighting technical rooms | - | -
13.1.2.8 | Escape lights | - | -
13.1.2.9 | Outdoor floodlights | - | -
13.1.2.10 | Outdoor street lights | - | -
13.1.2.11 | Outdoor fence lights | - | -
13.1.3 | Emergency Lighting Central Unit
13.1.3.1 | Manufacturer: | - | -
13.1.3.2 | Type: | - | -
13.1.3.3 | Central battery supply system | yes/no | yes
13.1.3.4 | Emergency Duration | h | 3
13.1.3.5 | Battery capacity | Ah | -
13.1.4 | Distribution boards
13.1.4.1 | Manufacturer | -
13.1.4.2 | Place of manufacture | -
13.1.4.3 | Model designation | -
13.1.4.4 | Applicable standard | - | IEC 61439, IEC 60947 etc. as per Employer's Requirements
13.1.4.5 | Internal separation | - | Form 2b
13.1.4.6 | Location of installation | - | indoor
13.1.4.7 | Number of phases | - | 3+N+PE
13.1.4.8 | Number of busbars | - | 1
13.1.4.9 | Nominal voltage | V AC | 230/400
13.1.4.10 | Rated frequency | Hz | 50
13.1.4.11 | Degree of Protection | - | IP54
13.1.4.12 | Instruments and accessories as per the Employer's Requirements | yes/no | yes
13.2 | Socket outlets, power outlets and plugs
13.2.1 | Manufacturer | - | -
13.2.2 | Type: | - | -
13.2.3 | 15 A, 230 V AC single-phase | - | -
13.2.4 | 32 A, 230/400 V AC three-phase | - | -
13.2.5 | Industrial type power outlet combination | - | -
13.2.6 | Power connection point | - | -
13.3 | Tests
13.3.1 | Tests according to relevant standards and Employer's Requirements | yes/no | yes

## 14. Fire Protection System
Technical Data Sheets
BIDDER’S / CONTRACTOR’S GUARANTEED DATA |  | Unit | Data required | Data offered
No. | Description
14. | Fire Protection System
14.1 | Fire Detection and Alarm System
14.1.1 | Fire Detection and Alarm System
14.1.1.1 | Applicable standard |  | EN 54 ISO 7240
14.1.1.2 | Manufacturer | -
14.1.1.3 | Origin of manufacture | -
14.1.1.4 | Type | -
14.1.2 | Fire Alarm and Control Panel
14.1.2.1 | Dimensions per cubicle L x W x H | mm
14.1.2.2 | Power requirements | VA
14.1.2.3 | Main supply voltage | V | 230
| Battery standby time | h | 72
14.1.2.4 | Operating voltage of fire alarm lines | V
14.1.2.5 | Maximum number of alarm lines possible | -
14.1.2.6 | Fault detection system for wire breakage | yes/no | yes
14.1.2.7 | Earth fault, short circuit detection | yes/no | yes
14.1.2.8 | Connection to SCADA | yes/no | yes
14.1.3 | Detectors
14.1.3.1 | Manufacturer | -
14.1.3.2 | Type | -
14.1.3.3 | Smoke Detetctor
14.1.3.4 | Heat Detector
14.1.3.5 | Flame Detector
14.1.3.6 | Manual Break Glass Unit
14.1.3 | Alarm Bells and Sounders
14.1.3.1 | Manufacturer | -
14.1.3.2 | Type
14.1.2.3 | Supply voltage | V (DC) | -
14.1.3.3 | Sound output at 3 m | dB(A) | 85
14.1.4 | Tests
14.1.4.1 | Tests according to relevant standards and Employer's Requirements | yes/no | yes
14.2 | Portable Fire Extinguishers
14.2.1 | Type: CO2 | -
14.2.1.1 | Number(s) | -
14.2.1.2 | Capacity of each | liters
14.2.2 | Type: dry chemical
14.2.2.1 | Number(s) | -
14.2.2.2 | Capacity of each | liters
14.3 | Wet Fire Fightung System
14.3.1 | Fire fighting water storage tank
14.3.1.1 | Applicable standard |  | BS EN 13280 BS EN 12845
14.3.1.2 | Manufacturer | -
14.3.1.3 | Type | -
14.3.1.4 | Material | - | GRP
14.3.1.5 | Storage Volume | m3 | >300
14.3.1.6 | Size ( h x w x d) | mm
14.3.2 | Fire fighting pump system container
14.3.2.1 | Manufacturer | -
14.3.2.2 | Type | -
14.3.2.3 | Total weight | kg
14.3.2.4 | Size ( h x w x d) | mm
14.3.3 | Fire pump electrical driven (100%)
14.3.3.1 | Manufacturer | -
14.3.3.2 | Type | -
14.3.3.3 | Rated capacity | m3/h | >280
14.3.3.4 | Rated discharge head | bar
14.3.3.5 | Motor voltage | V
14.3.3.6 | Motor rating | kW
14.3.4 | Fire pump diesel driven (100%)
14.3.4.1 | Manufacturer (pump) | -
14.3.4.2 | Type (pump) | -
14.3.4.3 | Rated capacity | m3/h | >280
14.3.4.4 | Rated discharge head | bar
14.3.4.5 | Manufacturer (diesel engine) | -
14.3.4.6 | Type (diesel engine) | -
14.3.4.7 | MCR of diesel engine | kW
14.3.4.8 | Fuel consumption | l/h
14.3.5 | Jockey pump
14.3.5.1 | Manufacturer | -
14.3.5.2 | Type | -
14.3.5.3 | Rated capacity | m3/h
14.3.5.4 | Rated discharge head | bar
14.3.5.5 | Motor voltage | V
14.3.5.6 | Motor rating | kW
14.3.6 | Transformer Spray Water System
14.3.6.1 | Manufacturer | -
14.3.6.2 | Type | -
14.3.6.3 | Application rate | l/min/m2 | 10.2

## 15. Metering
Technical Data Sheets
BIDDER’S / CONTRACTOR’S GUARANTEED DATA |  | Unit | Data required | Data offered
No. | Description
15 | Metering Equipment
15.1 | Electricity Meter
15.1.1 | Compliant to MID | yes/no | yes
15.1.2 | Compliant to IEC 62052-11 | yes/no | yes
15.1.3 | Compliant to IEC 62053-22 | yes/no | yes
15.1.4 | Compliant to IEC 62053-23 | yes/no | yes
15.1.5 | Manufacturer | -
15.1.6 | Origin of manufacture | -
15.1.7 | Type | -
15.1.8 | Specified operating range | °C | -20 to +55
15.1.9 | Limit range of operation | °C | -25 to +60
15.1.10 | Limit range for storage and transport | °C | - 25 to +70
15.1.11 | Protection Class according to IEC 60529 | IP | IP54
15.1.12 | Electrostatic discharges acc. to IEC 6100-4-2
15.1.12.1 | · Contact discharge | kV | 8
15.1.12.2 | · air discharge | kV | 15
15.1.13 | Electromagnetic RF Fields acc. IEC61000-4-3 80 MHz -2 GHz (with current / without any current) | V/m | 10/30
15.1.14 | Radio interferences suppression according to IEC/CISPR22 Class B | yes/no | yes
15.1.15 | Fast transient burst acc. to IEC61000-4-4
15.1.15.1 | · Current and voltage circuits | kV | 4
15.1.15.2 | · Auxiliary circuits >40V | kV | 2
15.1.16 | Standard Reference Voltage Un | V | 3x63,5/110
15.1.17 | Extended operating voltage range | V | 3x58/100 to 240/415 V
15.1.18 | Nominal frequency fn | Hz | 50
15.1.19 | Extended operating frequency range | % | ± 2
15.1.20 | Nominal current | A | 1
15.1.21 | Maximum current Imax | A | from 6 to 10
15.1.22 | Active energy measurement (according to MID) | - | class C
15.1.23 | Active energy measurement (according to IEC) | - | 0,2s
15.1.24 | Re-Active energy measurement (according to IEC) | - | 0.5
15.1.25 | Real-time clock according to IEC 62054-21 | yes/no | yes
15.1.26 | Measuring quadrants | - | 4
15.1.27 | Number of measuring elements | - | 3
15.1.28 | Meter lifecycle | years | ≥ 15
15.1.29 | Voltage failure bridging time | s | 0.5
15.1.30 | Voltage restoration function standby after | s | < 5
15.1.31 | Power consumption without communication
15.1.31.1 | · in the voltage circuit with power supply connected | W | ≤ 2
|  | VA | ≤ 5
15.1.31.2 | · in the current circuit at basic current Ib | VA | ≤ 4
15.1.32 | Insulation strength at 50Hz for 1 min | kV | 4
15.1.33 | Pulse voltage 1.2/50µs acc. to IEC62052-11 Current and voltage circuits | kV | ≥ 6
15.1.34 | Protection class acc. to IEC62052-11 | - | Class II
15.1.35 | Dimensions: Digitize in value field | mm | ≥ 8 mm
15.1.36 | Display of values: Programmable display sequence | yes/no | required
15.1.37 | LED test output for active and reactive energy | yes/no | required
15.1.38 | Optical interface acc. to IEC62056-21 | yes/no | required
15.1.39 | Optical interface communication ability | Baud | 9600
15.1.40 | RS 485 interface | Number | ≥ 1
15.1.41 | Communication protocols compliance with IEC 62056-21 and DIN EN 61107 requirements. | yes/no | yes
15.1.42 | DLMSCOSEM protocol (IEC 62056) | yes/no | yes
15.1.43 | Dimensions: | mm
15.1.43.1 | · height | mm
15.1.43.2 | · width | mm
15.1.43.3 | · depth | mm
15.1.43.4 | · Net weight | kg
15.1.44 | Heat resistance
15.1.44.1 | The terminal cover and the meter housing has to fulfill the heat resistance with tungsten filament test acc. IEC 60695 (temperature of 960°C) | yes/no | yes
15.1.45 | Meter cover seals
15.1.45.1 | At least one visible seal has to be provided in such a way that the internal parts of the meter are accessible only after breaking the seal(s). | yes/no | yes
15.1.46 | Meter Terminal seals
15.1.46.1 | At least one visible seal has to be provided and no access to the terminals shall be possible without breaking the seal(s) of the terminal cover(s). | yes/no | yes
15.1.47 | Units measured:
15.1.47.1 | kW forward, reverse | yes/no | yes
15.1.47.2 | kWh forward, reverse | yes/no | yes
15.1.47.3 | kWh forward + reverse | yes/no | yes
15.1.47.4 | kWh forward - reverse | yes/no | yes
15.1.47.5 | kVAr import, export | yes/no | yes
15.1.47.6 | kVArh import, export | yes/no | yes
15.1.47.7 | kVA forward, reverse | yes/no | yes
15.1.47.8 | kVAh forward, reverse | yes/no | yes
15.1.47.9 | RMS voltage per phase | yes/no | yes
15.1.47.10 | RMS current per phase | yes/no | yes
15.1.47.11 | Power factor per phase | yes/no | yes
15.1.47.12 | Phase angle for each phase | yes/no | yes
15.1.47.13 | Frequency | yes/no | yes
15.1.48 | Number of channels of remotely configurable load profile data that can be captured at programmable intervals. | - | ≥8
15.1.49 | Programmable intervals | yes/no | 5 to 60 min. / day
15.1.50 | Load profile storage capacity per channel | values | > 4000
15.1.51 | Long and short outage detection with date/time | yes/no | yes
15.1.52 | Min. voltage level register | yes/no | yes
15.1.53 | Over voltage register | yes/no | yes
15.1.54 | Under voltage register | yes/no | yes
15.1.55 | Harmonic analysis up to 30 harmonic | yes/no | yes
15.1.56 | Internal errors | yes/no | yes
15.1.57 | Communication problems | yes/no | yes
15.1.58 | Configuration problems | yes/no | yes
15.1.59 | Clock shift | yes/no | yes
15.1.60 | Power breaks | yes/no | yes
15.1.61 | Phase errors | yes/no | yes
15.1.62 | Overvoltage | yes/no | yes
15.1.63 | Undervoltage | yes/no | yes
15.1.64 | Meter tamper events | yes/no | yes
15.2 | Communication Equipment
15.2.1 | Manufacturer | -
15.2.2 | Origin of manufacture | -
15.2.3 | Type | -
15.2.4 | Compliant to IEC 60950 | yes/no | yes
15.2.5 | Compliant to IEC 62056-21 | yes/no | yes
15.2.6 | Compliant to IEC 61000-4-2 | yes/no | yes
15.2.7 | Compliant to IEC 61000-4-3 | yes/no | yes
15.2.8 | Compliant to IEC 61000-4-4 | yes/no | yes
15.2.9 | Compliant to IEC 61000-4-5 | yes/no | yes
15.2.10 | Compliant to IEC 61000-4-6 | yes/no | yes
15.2.11 | Compliant to IEC 61000-6-2 | yes/no | yes
15.2.12 | Compliant to IEC 61000-6-3 | yes/no | yes
15.2.13 | Meter built-in | yes/no | yes
15.2.14 | Antenna | yes/no | yes
15.2.15 | DLMS-COSEM protocol (IEC 62056) | yes/no | yes
15.3 | Metering panel
15.3.1 | Manufacturer | -
15.3.2 | Origin of manufacture
15.3.3 | Material | - | Galvanized steel
15.3.4 | Meter reading window material | - | Transparent Polycarbonate
15.3.5 | Overall dimensions
15.3.5.1 | · Height (from floor) | mm | ≤ 2000
15.3.5.2 | · Width | mm | ≤ 800
15.3.5.3 | · Depth | mm | ≥ 600 ≤ 300
15.3.5.4 | · Thickness (box) | mm | 2
15.3.5.5 | · Thickness (door) | mm | ≥ 1.5
15.3.6 | Protection degree (according to IEC 60529) | IP | ≥ IP 54
15.3.7 | Lockable | yes/no | yes
15.3.8 | Color | - | Light Grey (RAL-7035)
15.3.9 | Terminal blocks according to IEC 60947-7 | yes/no | yes

## 16. CCTV System
Technical Data Sheets
BIDDER’S / CONTRACTOR’S GUARANTEED DATA |  | Unit | Data required | Data offered
No. | Description
16. | CCTV System
16.1 | Fixed Perimeter Cameras
16.1.1 | Manufacturer
16.1.2 | Model designation
16.1.3 | Type | - | color
16.1.4 | Image format | -
16.1.5 | Focal length of lens | mm-mm
16.1.6 | Auto-focus lens | yes/no | yes
16.1.7 | Infrared Illumination | yes/no | yes
16.1.8 | Wide dynamic range | yes/no | yes
16.1.9 | Resolution | -
16.1.10 | Minimum sensitivity | lux | 0.02
16.1.11 | White balance control | yes/no | yes
16.1.12 | Automatic light control | yes/no | yes
16.1.13 | Back light compensation | yes/no | yes
16.1.14 | Coverage distance | m
16.1.15 | Minimum signal to noise ratio | dB | 50
16.1.16 | Exterior housing degree of protection | - | IP 66
16.1.17 | Junction box degree of protection | - | IP 65
16.2 | PTZ Cameras
16.2.1 | Manufacturer
16.2.2 | Model designation
16.2.3 | Type | - | color
16.2.4 | Image format | -
16.2.5 | Panning capability | degrees | 360º
16.2.6 | Panning speed | degrees/s | 6º
16.2.7 | Tilting capability | degrees | 180º
16.2.8 | Optical zoom | - | 20x
16.2.9 | Digital zoom | - | 10x
16.2.10 | Zoom speed | s
16.2.11 | Infrared Illumination | yes/no | yes
16.2.12 | Wide dynamic range | yes/no | yes
16.2.13 | Resolution | -
16.2.14 | Minimum sensitivity | lux | 0.02
16.2.15 | White balance control | yes/no | yes
16.2.16 | Automatic light control | yes/no | yes
16.2.17 | Back light compensation | yes/no | yes
16.2.18 | Minimum signal to noise ratio | dB | 50
16.2.19 | Exterior housing degree of protection | - | IP 66
16.2.20 | Junction box degree of protection | - | IP 65
16.3 | Ceiling Mounted Dome Cameras
16.3.1 | Manufacturer | -
16.3.2 | Model designation | -
16.3.3 | Type | - | color
16.3.4 | Focal length of lens | mm-mm
16.3.5 | Auto-focus lens | yes/no | yes
16.3.6 | Image format | -
16.3.7 | Infrared Illumination | yes/no | yes
16.3.8 | Wide dynamic range | yes/no | yes
16.3.9 | Back light compensation | yes/no | yes
16.3.10 | White balance control | yes/no | yes
16.3.11 | Automatic light control | yes/no | yes
16.3.12 | Minimum sensitivity | lux | 0.02
16.3.13 | Housing degree of protection | - | IP 42
16.4 | CCTV LAN
16.4.1 | LAN speed | Mbit/s | 1000
16.4.2 | Substation-hardened switches | yes/no | yes
16.4.3 | Manufacturer of central switch | -
16.4.4 | Model designation | -
16.4.5 | Manufacturer of disbursed switches | -
16.4.6 | Model designation | -
16.5 | CCTV Server
16.5.1 | Maximum number of controllable cameras | -
16.5.2 | Video and audio recording protocol | -
16.5.3 | Audio input and output | yes/no | yes
16.5.4 | Password protection | yes/no | yes
16.5.5 | Provision for communication with remote control center | yes/no | yes
16.5.6 | Equipped with all peripherals incl. monitor, keyboards, mouse etc. | yes/no | yes
16.5.7 | Interface for future connection allowing remote control from OST- NDC | yes/no | yes
16.6 | Digital Network Video Recorder System
16.6.1 | Video stream and storage management | yes/no | yes
16.6.2 | Period of recordings storage | days | 90
16.6.3 | Storage capacity | TB | 8
16.6.4 | RAID Configuration | - | RAID 1
16.7 | CCTV Workstations
16.7.1 | Number of monitors per workstation | - | 2
16.7.2 | Monitor type | - | LED
16.7.3 | Minimum monitor size | inches | 32
16.7.4 | Monitor manufacturer | -
16.7.5 | Model designation | -
16.7.6 | Equipped with all peripherals incl. monitor, keyboards, mouse etc. | yes/no | yes
16.7.7 | Color laser printer for video images, logs etc. | yes/no | yes
16.7.8 | Surveillance software:
16.7.9 | · number of displays on one screen | - | 16
16.7.10 | · sequential mode and multi-display mode | yes/no | yes
16.7.11 | · picture-in-picture analysis | yes/no | yes