PART 2A

EMPLOYER’S REQUIREMENTS FOR

SUBSTATION WORK

APPENDIX - A1: TECHNICAL PARTICULARS

This page is intentionally left blank.

APPENDIX - A1: TECHNICAL PARTICULARS

Table of Contents

CLAUSE NO.	TITLE	PAGE NO.

1	Electrical Works	1

1.1	Indoor Switchgear & Associated Equipment (145 kV)	1

1.1.1	High Voltage Gas Insulated Switchgear	1

1.1.2	Busbars	1

1.1.3	Circuit Breaker	2

1.1.4	Disconnecting Switch	4

1.1.5	Maintenance Earthing Switch	5

1.1.6	High Speed Earthing Switch	6

1.1.7	Current Transformer	6

1.1.8	Voltage Transformer	7

1.1.9	Local Control Unit for each switch bay	8

1.1.10	Gas Detector	8

1.2	INDOOR SWITCHGEAR & ASSOCIATED EQUIPMENT (12KV)	9

1.2.1	Medium Voltage Gas Insulated Switchgear	9

1.2.2	Busbars	9

1.2.3	Circuit Breaker	10

1.2.4	Disconnecting Switch	12

1.2.5	Maintenance Earthing Switch	13

1.2.6	Current Transformer	14

1.2.7	Voltage Transformer	15

1.2.8	Local Control Unit	15

1.3	LVAC EQUIPMENT	17

1.4	BATTERIES AND CHARGER	18

1.4.1	110V DC System	18

1.4.2	48V DC System	20

1.5	145 KV PROTECTION EQUIPMENT	23

1.5.1	132/11 kV Transformer Biased Differential Protection	23

1.5.2	Transformer Restricted Earth Fault Protection	23

1.5.3	Busbar Protection	24

1.5.4	Tripping Relays	24

1.5.5	Inverse Time Overcurrent and Earth Fault Protection	25

1.5.6	Line Differential Relay for 132 kV Overhead/Cable Line	26

1.5.7	Distance Protection for 132kV Overhead Lines / Cable	26

1.5.8	Dead Line Check Relays	28

1.5.9	Synchronising Check Relays	28

1.5.10	Breaker Failure Protection	28

1.5.11	Intercropping Send/Receiver Relays	29

1.5.12	Under Frequency Relay (If Applicable)	29

1.5.13	Relay Test Equipment	29

1.6	12 KV PROTECTION EQUIPMENT	30

1.6.1	Transformer Restricted Earth Fault Protection	30

1.6.2	Tripping Relays	30

1.6.3	Inverse Time Overcurrent & Earth Fault Protection	30

1.6.4	Dead Line Check Relays	31

1.6.5	Synchronising Check Relays	32

1.6.6	Under Frequency Relay	32

1.7	SUBSTATION AUTOMATION SYSTEM	33

1.8	FIBRE OPTIC & SCADA/TELECOMMUNICATION EQUIPMENT	34

1.8.1	SDH-Multiplexer (Fibre Optic Equipment)	34

1.8.2	VoIP Telephone System	35

1.9	GROUNDING MATERIALS	36

1.10	CABLES	37

1.10.1	1000V Cables（If Applicable）	37

1.10.2	Multicore Control Cables	37

1.10.3	132 kV Single Core XLPE Cable	38

1.10.4	Accessories of 132 kV Single Core XLPE Cable	44

1.10.5	11 kV Single Core XLPE Cable	47

1.10.6	Accessories of 11 kV Single Core 240mm2 XLPE Cable	51

1.11	TRANSFORMERS AND ASSOCIATED EQUIPMENT	53

1.11.1	30 MVA, 132/11 kV Transformer	53

1.11.2	Auxiliary Transformers 200kVA 11/0.4kV	64

1.11.3	Diesel Generator	66

1.11.4	Water Fire Fighting System for Transformer	66

1.11.5	Energy Meters	66

2	CIVIL WORKS	69

2.1	AIR CONDITIONING & VENTILATING INSTALLATIONS	69

2.1.1	Air Conditioning Units	69

2.1.2	Ventilation Works	70

2.2	FIRE SAFETY EQUIPMENT	70

2.3	LIGHTING & SMALL POWER	71

2.4	CCTV SYSTEM	73

2.5	LIGHTNING PROTECTION SYSTEM	74

2.6	INTRUDER PROTECTION SYSTEM	74

2.7	132KV GIS SUBSTATION	74

This page is intentionally left blank.

Electrical Works

Indoor Switchgear & Associated Equipment (145 kV)

| No. | Item |  |  |  | Units | Required 145kV | Tendered 145kV |
| --- | --- | --- | --- | --- | --- | --- | --- |
| High Voltage Gas Insulated Switchgear |  |  |  |  |  |  |  |
| 1 | Manufacturer’s Name |  |  |  |  | - |  |
| 2 | Country of Manufacture |  |  |  |  | - |  |
| 3. | Place of Testing |  |  |  |  | ‐ |  |
| 4. | Applicable Standard - IEC |  |  |  |  | ‐ |  |
| 5. | Manufacturer’s type designation, and type ref or model number |  |  |  |  | ‐ |  |
| 6. | Rated voltage |  |  |  | kV | 145 |  |
| 7. | Rated frequency |  |  |  | Hz | 50 |  |
| 8. | Maximum continuous system voltage at minimum gas pressure |  |  |  | kV | 145 |  |
| 9. | Impulse withstands voltage (peak) at minimum gas pressure |  |  |  | kV | 650 |  |
| 10. | Power frequency withstand voltage 1 min. at minimum gas pressure |  |  |  | kV | 275 |  |
| 11. | Power frequency withstand voltage at atmospheric pressure |  |  |  | kV |  |  |
| 12. | Rated short time withstand current |  |  |  | kA | 40 |  |
| 13. | Rated duration of short time withstand current |  |  |  | s | 1 |  |
| 14. | Rated peak short circuit current |  |  |  | kA |  |  |
| 15. | Heaviest part of any feeder for crane |  |  |  | kg |  |  |
| 16. | Feeder |  |  |  |  |  |  |
|  | - Width |  |  |  | mm |  |  |
|  | - Depth |  |  |  | mm |  |  |
|  | - Height |  |  |  | mm |  |  |
| 17. | Current SF6 gas replenishing |  |  |  | Yes/No | No |  |
| 18. | Annual leakage rate for each gas compartment |  |  |  | % | ≤0.1 |  |
| 19. | Material of filter employed for moisture absorption |  |  |  |  |  |  |
| 20. | Heat losses per feeder at rated Power |  |  |  |  |  |  |
| Busbars |  |  |  |  |  |  |  |
| 1 | Rated normal current |  |  |  | A | 3150 |  |
| 2. | Rated current at max. ambient temperature |  |  |  | A |  |  |
| 3. | Conductor Material |  |  |  |  |  |  |
| 4. | Standard applicable |  |  |  |  |  |  |
| 5. | Single conductor cross section |  |  |  | mm² |  |  |
| Circuit Breaker |  |  |  |  |  |  |  |
| 1. | Manufacturer’s Name |  |  |  |  |  |  |
| 2. | Manufacture’s Address |  |  |  |  |  |  |
| 3. | Manufacturer’s Type Designation |  |  |  |  |  |  |
| 4. | Applicable Standard |  |  |  |  |  |  |
| 5. | Type tested |  |  |  | Yes/No | Yes |  |
| 6. | Type test report, Ref. No. |  |  |  |  |  |  |
| 4. | Rated normal current at 20°C |  |  |  |  |  |  |
|  | - line feeder circuit breaker |  |  |  | A | 2000 |  |
|  | - bus coupler / section circuit breaker |  |  |  | A | 3150 |  |
|  | - 132kV/11kV transformer circuit |  |  |  | A | 1250 |  |
| 5. | Rated current at max. ambient temperature |  |  |  | A |  |  |
|  | - line feeder circuit breaker |  |  |  | A | 2000 |  |
|  | - bus coupler / section circuit breaker |  |  |  | A | 3150 |  |
|  | - 132kV/11kV transformer circuit breaker |  |  |  | A | 1250 |  |
| 6. | Rated short circuit breaking current (symmetrical, r.m.s.) |  |  |  | kA | 40 |  |
| 7. | Rated short circuit breaking current (asymmetrical, r.m.s.) |  |  |  | kA | 40 |  |
| 8. | Rated short circuit making current (peak) |  |  |  | kA | 40 |  |
| 9. | Rated cable charging breaking current |  |  |  | A |  |  |
| 10. | Rated line charging breaking current |  |  |  | A |  |  |
| 11. | Rated small inductive breaking current |  |  |  | A |  |  |
| 12 | Voltage drops across terminals of one pole at rated current |  |  |  | mV |  |  |
| 13. | Amplitude factor |  |  |  |  |  |  |
| 14. | First pole-to-clear factor |  |  |  |  | 1.5 |  |
| 15. | Rated operating sequence: |  |  |  |  | O-t-CO-t'-CO |  |
|  | - with t |  |  |  | sec. | 0.3 |  |
|  | - with t' |  |  |  | min. | 3 |  |
| 16. | Min. time t" between two successful three phase auto reclosures at full rated breaking current (sequence O-t-C-t"-O-t-C) |  |  |  | min. |  |  |
| 17. | Closing time |  |  |  | ms |  |  |
|  | - tolerances |  |  |  | ms |  |  |
| 18. | Dead time (max.) |  |  |  | ms |  |  |
|  | - tolerances |  |  |  | ms |  |  |
| 19. | Break time (max.) at full rated breaking current |  |  |  | ms |  |  |
|  | - tolerances |  |  |  | ms |  |  |
| 20. | Make time (max.) |  |  |  | ms |  |  |
|  | - tolerances |  |  |  | ms |  |  |
| 21 | Arcing time (max.) at full short circuit duty |  |  |  | ms |  |  |
|  | - tolerances |  |  |  | ms |  |  |
| 22. | Life duration of main contacts (no load mechanical operations) |  |  |  | operations |  |  |
| 23. | Number of switching operations at rated breaking capacity before contact maintenance becomes necessary |  |  |  | No. | min. 10 |  |
| 24 | Rated pressure of SF6 for arc quenching |  |  |  | bar |  |  |
| 25. | Auxiliary contacts: |  |  |  |  |  |  |
|  | - number (NO/NC) |  |  |  |  |  |  |
|  | - voltage rating |  |  |  | V DC | 110 |  |
|  | - current rating |  |  |  | A DC |  |  |
| 26. | SF6 pressure at which lockout operates |  |  |  | bar |  |  |
| 27. | To be filled in only in case of hydraulic operating mechanism: |  |  |  |  |  |  |
|  | - Setting of pressure relief device |  |  |  | bar |  |  |
|  | - Rated pressure of hydraulic oil |  |  |  | bar |  |  |
|  | - Lowest oil pressure at which lockout |  |  |  | bar |  |  |
| 28. | Making coil |  |  |  |  |  |  |
|  | - Rated voltage |  |  |  | V DC | 110 |  |
|  | - min. operating voltage |  |  |  | V | 88 |  |
|  | - Rated power each |  |  |  | W |  |  |
| 29. | Trip coil |  |  |  |  |  |  |
|  | - Rated voltage |  |  |  | V DC | 110 |  |
|  | - min. operating voltage |  |  |  | V | 88 |  |
|  | - Rated power each |  |  |  | W |  |  |
| 30. | Motor voltage |  |  |  | V DC | 110 |  |
| 31. | Motor power |  |  |  | W |  |  |
| 32. | Total loss of heaters for 3 poles |  |  |  | W |  |  |
| 33. | Max. temperature rise of contacts at rated normal Current |  |  |  | K |  |  |
| 34. | Arc quenching medium |  |  |  |  | SF₆ |  |
| 35. | Material of main contacts |  |  |  |  |  |  |
| 36 | Number of breaks in series (per pole) |  |  |  | No. |  |  |
|  | - for closing |  |  |  |  |  |  |
|  | - for opening |  |  |  |  |  |  |
| 37. | Single pole operation (only in Line Feeder Breakers) |  |  |  | Yes/No | No |  |
| 38. | Making coil: |  |  |  |  |  |  |
|  | - number |  |  |  | pcs |  |  |
| 39. | Trip coil: |  |  |  |  |  |  |
|  | - number |  |  |  | pcs | 2 |  |
| 40. | Gas quantity of complete breaker (3 Phase) |  |  |  | kg |  |  |
| 41. | Material of filter employed for the absorption of the products of combustion |  |  |  |  |  |  |
| 42. | Method of controlling voltage distribution between breaks (capacitor, resistor etc.) |  |  |  |  |  |  |
| 43. | Weight of complete 3 pole breaker |  |  |  | kg |  |  |
| 44. | Weight of heaviest part for shipment |  |  |  | kg |  |  |
| Disconnecting Switch |  |  |  |  |  |  |  |
| 1. | Model No. |  |  |  |  |  |  |
| 2. | Type tested |  |  |  | Yes/No | Yes |  |
| 3. | Type test report, Ref. No. |  |  |  |  |  |  |
| 4. | Standards to which disconnector conforms |  |  |  |  | IEC 60129 |  |
| 5. | Power frequency withstand voltage across isolating distance |  |  |  | kV | 315 |  |
| 6. | Lightning impulse withstand voltage across isolating distance |  |  |  | kV | 750 |  |
| 7. | Rated normal current at 20°C |  |  |  |  |  |  |
|  | - feeder disconnecting switch |  |  |  | A | 2000 |  |
|  | - bus coupler / section disconnecting switch |  |  |  | A | 2000 |  |
|  | -132/11kV transformer feeder disconnecting switch |  |  |  | A | 1250 |  |
| 8. | Rated current at max. ambient temperature: |  |  |  |  |  |  |
|  | -line feeder disconnecting switch |  |  |  | A | 2000 |  |
|  | - bus coupler / section disconnecting switch |  |  |  | A | 2000 |  |
|  | - transformer feeder disconnecting switch |  |  |  | A | 1250 |  |
| 9. | Voltage drops across terminals of one pole at rated current |  |  |  | mV |  |  |
| 10. | Rated breaking current (capacitive) |  |  |  | A |  |  |
| 11. | Rated momentary current (peak) |  |  |  | kV |  |  |
| 12. | Life duration of main contacts |  |  |  | operations |  |  |
| 13. | Material of main contacts |  |  |  |  |  |  |
| 14. | Auxiliary contacts: |  |  |  |  |  |  |
|  | - number (NO/NC) |  |  |  | pcs/pcs |  |  |
|  | - voltage rating |  |  |  | V DC | 110 |  |
|  | - current rating |  |  |  | A DC |  |  |
| 15. | Operating mechanism: |  |  |  |  |  |  |
|  | - for closing |  |  |  |  | Electric motor |  |
|  | - for opening |  |  |  |  | Electric motor |  |
| 16. | Manual operating facility |  |  |  | Yes/No | Yes |  |
| 17. | Motor voltage |  |  |  | V DC | 110 |  |
| 18. | Motor power |  |  |  | W |  |  |
| 19. | Hand operating facilities |  |  |  | Yes/No |  |  |
| 20. | Weight |  |  |  |  |  |  |
|  | - 3 phase unit with driving mechanism |  |  |  | kg |  |  |
| 21. | Mechanism heater loss |  |  |  | W |  |  |
| Maintenance Earthing Switch |  |  |  |  |  |  |  |
| 1. |  | Type tested |  |  | Yes/No | Yes |  |
| 2. |  | Type test report, Ref. No. |  |  |  |  |  |
| 3. |  | Standards to which earthing switch conforms |  |  |  |  |  |
| 4. |  | Life duration of main contacts |  |  | operations |  |  |
| 5. |  | Material of main contacts |  |  |  |  |  |
| 6. |  | Auxiliary contacts: |  |  |  |  |  |
|  |  | - number (NO/NC) |  |  | pcs/pcs |  |  |
|  |  | - voltage |  |  | V DC | 110 |  |
| 7. |  | Operating mechanism: |  |  |  |  |  |
|  |  | - for opening |  |  |  | Electric motor |  |
|  |  | - for closing |  |  |  | Electric motor |  |
| 8. |  | Motor voltage |  |  | V DC | 110 |  |
| 9. |  | Motor power |  |  | W |  |  |
| 10. |  | Hand operating facilities |  |  | Yes/No | Yes |  |
| High Speed Earthing Switch |  |  |  |  |  |  |  |
| 1. |  |  | Type tested |  | Yes/No | Yes |  |
| 2. |  |  | Type test report, Ref. No. |  |  |  |  |
| 3. |  |  | Standards to which earthing switch conforms |  |  |  |  |
| 4. |  |  | Making current |  | kA r.m.s | 40 |  |
| 5. |  |  | Number of closing operations with maximum short circuit current before the contact maintenance becomes necessary |  | No | 2 |  |
| 6. |  |  | Short circuit withstand duration |  | s | 1 |  |
| 7. |  |  | Life duration of main contacts |  | operations |  |  |
| 8. |  |  | Material of main contacts |  |  |  |  |
| 9. |  |  | Auxiliary contacts: |  |  |  |  |
|  |  |  | - number (NO/NC) |  | pcs/pcs |  |  |
|  |  |  | - voltage |  | V DC | 110 |  |
| 10. |  |  | Operating mechanism: |  |  |  |  |
|  |  |  | - for closing |  |  |  |  |
|  |  |  | - for opening |  |  |  |  |
| 11. |  |  | Max. Operating time |  |  |  |  |
|  |  |  | - for closing |  | ms |  |  |
|  |  |  | - for opening |  | ms |  |  |
| 12. |  |  | Motor voltage |  | V DC | 110 |  |
| 13. |  |  | Motor power |  | W |  |  |
| 14. |  |  | Hand operating facilities |  | Yes/No | Yes |  |
| Current Transformer |  |  |  |  |  |  |  |
| 1. |  |  |  | Type |  |  |  |
| 2. |  |  |  | Standards to which CT conforms | IEC | 60044-1 |  |
| 3. |  |  |  | Rated secondary current | A | 1 |  |
| 4. |  |  |  | Rated primary current and number of cores | A | See Scope of Works and drawings |  |
| 5. |  |  |  | Rated momentary current (peak) | kA | 100 |  |
| 6. |  |  |  | Rated short-time current | kA | 40 |  |
| 7. |  |  |  | Measuring cores: |  |  |  |
|  |  |  |  | - Accuracy class |  | 0.5 |  |
|  |  |  |  | - Burden |  |  |  |
|  |  |  |  | - Resistance of secondary winding at 75 °C | Ohms |  |  |
|  |  |  |  | - Instrument security factor |  |  |  |
| 8. |  |  |  | Protection cores: |  |  |  |
|  |  |  |  | - accuracy class protection cores min. (higher class to be used wherever necessitated due to protection requirements) |  | 5P |  |
|  |  |  |  | - Resistance of secondary winding protection cores at 75 °C | Ohms |  |  |
|  |  |  |  | - Resistance of secondary winding busbar protection cores at 75 °C | Ohms |  |  |
| 9. |  |  |  | Number of cores | Nos. | See Scope of Works and drawings |  |
| 10. |  |  |  | Knee point e.m.f. of protection cores | V |  |  |
| 11. |  |  |  | Knee point e.m.f. of busbar protection cores | V |  |  |
| 12. |  |  |  | Insulation material for windings |  |  |  |
| 13. |  |  |  | Limits on exciting current |  |  |  |
| 14 |  |  |  | Partial discharge |  | According to IEC 60044-1 |  |
| Voltage Transformer |  |  |  |  |  |  |  |
| 1. |  |  |  | Type |  |  |  |
| 2. |  |  |  | Standards | IEC | IEC 60044-2 |  |
| 3. |  |  |  | Method of transformation (inductive or capacitive) |  | inductive |  |
| 4. |  |  |  | Nominal primary voltage | kV | 132/√3 |  |
| 5 |  |  |  | Number of secondaries and accuracy class |  | See Scope of Works & Drawings |  |
| 6 |  |  |  | Thermal capacity of ground-fault detection winding | A/h |  |  |
| 7 |  |  |  | Rated burden (total on all secondaries) | VA |  |  |
| 8. |  |  |  | Partial discharge |  | According to IEC 60044-2 |  |
| 9. |  |  |  | Height | mm |  |  |
| 10. |  |  |  | Weight of single pole unit | kg |  |  |
| Local Control Unit for each switch bay |  |  |  |  |  |  |  |
| 1. |  |  |  | Type |  |  |  |
| 2. |  |  |  | Manufacturer |  |  |  |
| 3. |  |  |  | Standards |  |  |  |
| 4. |  |  |  | Material |  |  |  |
| 5. |  |  |  | Thickness | mm |  |  |
| 6. |  |  |  | Surface finish |  |  |  |
| 7. |  |  |  | Dimensions: - |  |  |  |
|  |  |  |  | length | mm |  |  |
|  |  |  |  | width | mm |  |  |
|  |  |  |  | height | mm |  |  |
| 8. |  |  |  | Total net mass | kg |  |  |
| Gas Detector |  |  |  |  |  |  |  |
| 1. |  |  |  | Manufacturer | - |  |  |
| 2. |  |  |  | Type | - |  |  |

INDOOR SWITCHGEAR & ASSOCIATED EQUIPMENT (12KV)

| No. | Item | Units |  | Required 12kV | Tendered 12kV |
| --- | --- | --- | --- | --- | --- |
| Medium Voltage Gas Insulated Switchgear |  |  |  |  |  |
| 1. | Manufacturer’s Name |  |  |  |  |
| 2. | Country of Manufacture |  |  |  |  |
| 3. | Place of Testing |  |  |  |  |
| 4. | Applicable Standard - IEC |  |  |  |  |
| 5. | Manufacturer’s type designation and type ref. or model number |  |  |  |  |
| 6. | Rated voltage | kV |  | 12 |  |
| 7. | Rated frequency | Hz |  | 50 |  |
| 8. | Maximum continuous system voltage at minimum gas pressure | kV |  | 12 |  |
| 9. | Impulse withstands voltage (peak) at minimum gas pressure | kV |  | 75 |  |
| 10. | Power frequency withstand voltage 1 min. at minimum gas pressure | kV |  | 28 |  |
| 11. | Power frequency withstand voltage 1 min. at atmospheric pressure | kV |  |  |  |
| 12. | Rated short time withstand current: | kA |  | 25 |  |
| 13. | Rated duration of short time withstand current: | s |  | 3 |  |
| 14. | Rated peak short circuit current | kA |  |  |  |
| 15. | Heaviest part of any feeder for crane | kg |  |  |  |
| 16. | Feeder |  |  |  |  |
|  | - Width: | mm |  |  |  |
|  | - Depth: | mm |  |  |  |
|  | - Height: | mm |  |  |  |
| 17. | Current SF6 gas replenishing | Yes/No |  | No |  |
| 18. | Annual leakage rate for each gas compartment |  | % | ≤0.1 |  |
| 19. | Material of filter employed for moisture absorption |  |  |  |  |
| 20. | Heat losses per feeder at rated Power | kW |  |  |  |
| Busbars |  |  |  |  |  |
| 1. | Rated normal current | A |  | 3000 |  |
| 2. | Rated current at max. ambient temperature | A |  | 3000 |  |
| 3. | Conductor material |  |  |  |  |
| 4. | Standard applicable |  |  |  |  |
| 5. | Single conductor cross section | mm² |  |  |  |
| Circuit Breaker |  |  |  |  |  |
| 1. | Manufacturer’s Name |  |  |  |  |
| 2. | Manufacture’s Address |  |  |  |  |
| 3. | Manufacturer’s Type Designation |  |  |  |  |
| 4. | Applicable Standard |  |  |  |  |
| 5. | Type tested | Yes/No |  | Yes |  |
| 6. | Type test report, Ref. No. |  |  |  |  |
| 4. | Rated normal current at 20°C |  |  |  |  |
|  | - line & aux. t/f /sub t line feeder circuit breaker | A |  | 630/1200 |  |
|  | - transformer feeder circuit breaker | A |  | 2500 |  |
|  | - bus section circuit breaker | A |  | 3150 |  |
| 5. | Rated current at max. ambient temperature | A |  |  |  |
|  | - line & aux. t/f/sub t line feeder/ line circuit breaker | A |  | 630/1200 |  |
|  | - transformer feeder circuit breaker | A |  | 2500 |  |
|  | - bus section circuit breaker | A |  | 3150 |  |
| 6. | Rated short circuit breaking current (symmetrical, r.m.s.) | kA |  | 25 |  |
| 7. | Rated short circuit breaking current (asymmetrical, r.m.s.) | kA |  | 25 |  |
| 8. | Rated short circuit making current (peak) | kA |  | 78.75 |  |
| 9. | Rated cable charging breaking current | A |  |  |  |
| 10. | Rated line charging breaking current | A |  |  |  |
| 11. | Rated small inductive breaking current | A |  |  |  |
| 12. | Voltage drops across terminals of one pole at rated current | mV |  |  |  |
| 13. | Amplitude factor |  |  |  |  |
| 14. | Frist pole –to-clear factor |  |  | 1.5 |  |
| 15. | Rated operating sequence: |  |  | O-t-CO-t'-CO |  |
|  | - with t | sec. |  | 0.3 |  |
|  | - with t' | min. |  | 3 |  |
| 16. | Min. time t" between two successful three phase auto reclosures at full rated breaking current (sequence O-t-C-t"-O-t-C) | min. |  |  |  |
| 17. | Closing time | ms |  |  |  |
|  | - tolerances | ms |  |  |  |
| 18. | Dead time (max.) | ms |  |  |  |
|  | - tolerances | ms |  |  |  |
| 19. | Break time (max.) at full rated breaking current | ms |  |  |  |
|  | - tolerances | ms |  |  |  |
| 20. | Make time (max.) | ms |  |  |  |
|  | - tolerances | ms |  |  |  |
| 21. | Arcing time (max.) at full short circuit duty | ms |  |  |  |
|  | - tolerances | ms |  |  |  |
| 22. | Life duration of main contacts (no load mechanical operations) | operations |  |  |  |
| 23. | Number of switching operations at rated breaking capacity before contact maintenance becomes necessary | No. |  | min. 25 |  |
| 24. | skip |  |  |  |  |
| 25 | Auxiliary contacts: |  |  |  |  |
|  | - number (NO/NC) |  |  |  |  |
|  | - voltage rating | V DC |  | 110 |  |
|  | - current rating | A DC |  |  |  |
| 26. | SF6 pressure at which lockout operates | bar |  |  |  |
| 27. | To be filled in only in case of hydraulic operating mechanism: |  |  |  |  |
|  | - Setting of pressure relief device | bar |  |  |  |
|  | - Rated pressure of hydraulic oil | bar |  |  |  |
|  | - Lowest oil pressure at which lockout |  |  |  |  |
| 28. | Making coil |  |  |  |  |
|  | - Rated voltage | V DC |  | 110 |  |
|  | - Min. operating voltage | V |  | 88 |  |
|  | - Rated power each | W |  |  |  |
| 29. | Trip coil |  |  |  |  |
|  | - Rated voltage | V DC |  | 110 |  |
|  | - Min. operating voltage | V |  | 88 |  |
|  | - Rated power each | W |  |  |  |
| 30. | Motor voltage | V DC |  | 110 |  |
| 31. | Motor power | W |  |  |  |
| 32. | Total loss of heaters for 3 poles | W |  |  |  |
| 33. | Max. temperature rise of contacts at rated normal Current | K |  |  |  |
| 34. | Arc. quenching medium |  |  | vacuum |  |
| 35. | Material of main contacts |  |  |  |  |
| 36. | Number of breaks in series (per pole) | No. |  |  |  |
|  | - For closing |  |  |  |  |
|  | - For opening |  |  |  |  |
| 37. | Single pole operation (only in Line Feeder Breakers) | Yes/No |  | No |  |
| 38. | Making coil: |  |  |  |  |
|  | - Number | pcs |  |  |  |
| 39. | Trip coil: |  |  |  |  |
|  | - Number | pcs |  | 2 |  |
| 40. | Gas quantity of complete breaker (3 Phase) | kg |  |  |  |
| 41. | Material of filter employed for the absorption of the products of combustion |  |  |  |  |
| 42. | Method of controlling voltage distribution between breaks (capacitor, resistor etc.) |  |  |  |  |
| 43. | Weight of complete 3 pole breaker | kg |  |  |  |
| 44. | Weight of heaviest part for shipment | kg |  |  |  |
| Disconnecting Switch |  |  |  |  |  |
| 1. | Model No. |  |  |  |  |
| 2. | Type tested | Yes/No |  | Yes |  |
| 3. | Type test report, Ref. No. |  |  |  |  |
| 4. | Standards to which disconnector conforms |  |  | 62271-200 |  |
| 5. | Power frequency withstand voltage across isolating distance | kV |  | 32 |  |
| 6. | Lighting impulse withstand voltage across isolating distance | kV |  | 85 |  |
| 7. | Rated normal current at 20 °C |  |  |  |  |
|  | - Line and aux.t/f/sub t line feeder disconnecting switch | A |  | 630/1200 |  |
|  | - Bus section disconnecting switch | A |  | 3150 |  |
|  | - Transformer feeder disconnecting switch | A |  | 2500 |  |
| 8. | - Rated current at max. ambient temperature: |  |  |  |  |
|  | - Line and aux.t/f/sub t line feeder disconnecting switch | A |  | 630/1200 |  |
|  | - Bus section disconnecting switch | A |  | 3150 |  |
|  | - Transformer feeder disconnecting switch | A |  | 2500 |  |
| 9. | Voltage drops across terminals of one pole at rated current | mV |  |  |  |
| 10. | Rated breaking current (capacitive) | A |  |  |  |
| 11. | Rated momentary current (peak) | kA |  |  |  |
| 12. | Lite duration of main contacts | operations |  |  |  |
| 13. | Material of main contacts |  |  |  |  |
| 14. | Auxiliary contacts: |  |  |  |  |
|  | - number (NO/NC) | pcs/pcs |  |  |  |
|  | - voltage rating | V DC |  | 110 |  |
|  | - current rating | A DC |  |  |  |
| 15. | Operating mechanism: |  |  |  |  |
|  | - for closing |  |  | electric motor |  |
|  | - for opening |  |  | electric motor |  |
| 16. | Manual operating facility | Yes/No |  | Yes |  |
| 17. | Motor voltage | V DC |  | 110 |  |
| 18. | Motor power | W |  |  |  |
| 19. | Hand operating facilities | Yes/No |  |  |  |
| 20. | Weight |  |  |  |  |
|  | - 3 phase unit with driving mechanism | kg |  |  |  |
| 21. | Mechanism heater loss | W |  |  |  |
| Maintenance Earthing Switch |  |  |  |  |  |
| 1. | Type tested | Yes/No |  | Yes |  |
| 2. | Type test report, Ref. No. |  |  |  |  |
| 3. | Standards to which earthing switch conforms |  |  |  |  |
| 4. | Life duration of main contacts | operations |  |  |  |
| 5. | Material of main contacts |  |  |  |  |
| 6. | Auxiliary contacts: |  |  |  |  |
|  | - number (NO/NC) | pcs/pcs |  |  |  |
|  | - voltage | V DC |  | 110 |  |
| 7. | Operating mechanism: |  |  |  |  |
|  | - for opening |  |  | Electric motor |  |
|  | - for closing |  |  | Electric motor |  |
| 8. | Motor voltage | V DC |  | 110 |  |
| 9. | Motor power | W |  |  |  |
| 10. | Hand operating facilities | Yes/No |  | Yes |  |
| Current Transformer |  |  |  |  |  |
| 1. | Type |  |  |  |  |
| 2. | Standards to which CT conforms | IEC |  | 60044-1 |  |
| 3. | Rated secondary current | A |  | 1 |  |
| 4. | Rated primary current and number of cores | A |  | See Scope of Works and drawings |  |
| 5. | Rated secondary current (peak) | kA |  |  |  |
| 6. | Rated short-time current | kA |  |  |  |
| 7. | Measuring cores: |  |  |  |  |
|  | - Accuracy class |  |  | 0.5 |  |
|  | - Burden |  |  |  |  |
|  | - Resistance of secondary winding at 75°C | Ohms |  |  |  |
|  | - Instrument security factor |  |  |  |  |
| 8. | Metering cores: |  |  |  |  |
|  | - Accuracy class |  |  | 0.2 |  |
|  | - Burden |  |  |  |  |
|  | - Instrument security factor |  |  |  |  |
| 9. | - Protection cores: |  |  |  |  |
|  | - Accuracy class protection cores min. (higher class to be used wherever necessitated due to protection requirement) |  |  | 5P |  |
|  | - Resistance of secondary winding protection cores at 75°C | Ohms |  |  |  |
|  | - Resistance of secondary winding busbar protection cores at 75°C | Ohms |  |  |  |
| 10. | Number of cores | Nos. |  | See Scope of Works and drawings |  |
| 11. | Knee point e.m.f. of protection cores | V |  |  |  |
| 12. | Knee point e.m.f. of busbar protection cores | V |  |  |  |
| 13. | Insulation material for windings |  |  |  |  |
| 14. | Limits on exciting current | A |  |  |  |
| 15. | Partial discharge |  |  | According to IEC 60044-1 |  |
| Voltage Transformer |  |  |  |  |  |
| 1. | Type |  |  |  |  |
| 2. | Standards | IEC |  | IEC 60044-2 |  |
| 3. | Method of transformation (inductive or capacitive) |  |  | inductive |  |
| 4. | Nominal primary voltage | kV |  | 11/√3 |  |
| 5. | Number of secondaries and accuracy class |  |  | See Scope of Works & Drawings |  |
| 6. | Thermal capacity of ground-fault detection winding | A/h |  |  |  |
| 7. | Rated burden (total on all secondaries) | VA |  |  |  |
| 8. | Partial discharge |  |  | acc. IEC 60044-2 |  |
| 9. | Height | mm |  |  |  |
| 10. | Weight of single pole unit | kg |  |  |  |
| Local Control Unit |  |  |  |  |  |
| 1. | Type |  |  |  |  |
| 2. | Manufacturer |  |  |  |  |
| 3. | Standards |  |  |  |  |
| 4. | Material |  |  |  |  |
| 5. | Thickness | mm |  |  |  |
| 6. | Surface finish |  |  |  |  |
| 7. | Dimensions: - |  |  |  |  |
|  | length | mm |  |  |  |
|  | width | mm |  |  |  |
|  | height | mm |  |  |  |
| 8. | Total net mass | kg |  |  |  |

LVAC EQUIPMENT

| No. | Item | Units | Required | Tendered |
| --- | --- | --- | --- | --- |
| (a) | DISTRIBUTION BOARD |  |  |  |
| 1. | Manufacturer's Name |  |  |  |
| 2. | Manufacturer's Address |  |  |  |
| 3. | Manufacturer’s type designation and type ref number or Model number |  |  |  |
| 4. | Rating | A | 1000 |  |
| 5. | Fault Rating | kA | 16 |  |
| 6. | Voltage | V | 400/230 |  |
| (b) | MCCB |  |  |  |
| 1. | Manufacturer's Name |  |  |  |
| 2. | Manufacturer's Address |  |  |  |
| 3. | Manufacturer’s type designation and type ref number or Model number |  |  |  |
| 4. | Type |  |  |  |
| 5. | Rating | A |  |  |
| 6. | Fault Rating | kA | 16 |  |
| (c) | ACB |  |  |  |
| 1. | Manufacturer's Name |  |  |  |
| 2. | Manufacturer's Address |  |  |  |
| 3. | Manufacturer’s type designation and type ref number or Model number |  |  |  |
| 4. | Type |  |  |  |
| 5. | Rating | A |  |  |
| 6. | Fault Rating | kA | 16 |  |

BATTERIES AND CHARGER

| No. | Item | Units | Required 110V | Tendered 110V |
| --- | --- | --- | --- | --- |
| 110V DC System |  |  |  |  |
| (a) | Battery |  |  |  |
| 1. | Manufacturer's Name |  |  |  |
| 2. | Country of Manufacture |  |  |  |
| 3. | Place of Testing |  |  |  |
| 4. | Applicable Standard - IEC |  | 60623 |  |
| 5. | Manufacturer’s type designation, and type ref or model number |  | NiCd |  |
| 6. | Voltage | V DC | 110 |  |
| 7. | Capacity at 10-hour rate | Ah | 300 |  |
| 8. | Number of cells |  |  |  |
| 9. | Voltage per cell | V |  |  |
| 10. | Battery voltage at end of the duty cycle | V |  |  |
| 11. | Normal charging rate | A |  |  |
| 12. | Maximum charging rate | A |  |  |
| 13. | Ampere-hour efficiency at ten-hour rate | % |  |  |
| 14. | Ampere-hour efficiency at one hour rate | % |  |  |
| 15. | Dimensions of cells | mm |  |  |
| 16. | Dimensions of battery complete | mm |  |  |
| 17. | Weight of cell complete with electrolyte | kg |  |  |
| 18. | Total weight of battery complete | kg |  |  |
| 19. | Internal resistance per cell when fully charged | ohms |  |  |
| 20. | Material of battery case |  |  |  |
| (b) | Battery Charger |  |  |  |
| 1. | Manufacturer’s name |  |  |  |
| 2. | Manufacturer’s address |  |  |  |
| 3. | Place of Testing |  |  |  |
|  | Type |  | NiCd |  |
| 4. | Manufacturer’s type designation and type ref number or model number |  |  |  |
| 5. | Applied standard |  |  |  |
| 6. | Number of phases | Three | 3 |  |
| 7. | Type of charger control | Micro processor |  |  |
| 8. | AC Input Nominal Voltage | V | 400 |  |
| 9. | AC Input Voltage range | % |  |  |
| 10. | Operating frequency | Hz |  |  |
| 11. | AC input to charger at full load | kVA |  |  |
| 12. | AC input current | A |  |  |
| 13. | DC Nominal Voltage | V | 110 |  |
| 14. | DC output of the charger | kW |  |  |
| 15. | Constant voltage |  |  |  |
|  | (i) Floating charge | V |  |  |
|  | (ii) Equalizing charge | V |  |  |
| 16. | Maximum output voltage |  |  |  |
|  | (i) at automatic control | V |  |  |
|  | (ii) at Boost charge | V |  |  |
| 17. | Regulation | % |  |  |
| 18. | Range of DC voltage control |  |  |  |
| 19. | Output voltage ripple | % | 4 |  |
| 20. | Protection class |  | IP 51 |  |
| 21. | Operating ambient temperature | °C | 45 |  |
| 22. | Dimension |  |  |  |
|  | (i) Height | mm |  |  |
|  | (ii) Width | mm |  |  |
|  | (iii) Depth | mm |  |  |
| 23. | Normal and Boost charge are Independent Units | Yes/No |  |  |
| 24. | Test report reference No: |  |  |  |
| (c) | 110V D.C. Switchboards |  |  |  |
| 1. | Manufacturer's Name |  |  |  |
| 2. | Manufacturer's Address |  |  |  |
| 3. | Place of Testing |  |  |  |
| 4. | Type of construction |  |  |  |
| 5. | Manufacturer’s type designation and type ref number |  |  |  |
| 6.. | Busbars: - |  |  |  |
|  | (i) Maximum current rating | A |  |  |
|  | (ii) Dimensions | mm |  |  |
| 7. | Boost charge contactors: - |  |  |  |
|  | (i) Manufacturer |  |  |  |
|  | (ii) Maximum current rating | A |  |  |
|  | (iii) Coil rating | W |  |  |
|  | (iv) Method of interlocking |  |  |  |
| 8. | Alarm relays: - |  |  |  |
|  | (i) Manufacturer |  |  |  |
|  | (ii) Type and reference |  |  |  |
|  | (iii) Power consumption: - |  |  |  |
|  | a) Quiescent | A |  |  |
|  | b) Operated | mA |  |  |
| 9. | Number and rating of distribution circuits |  |  |  |
| 10. | Overall dimensions | mm |  |  |
| 11. | Total weight | kg |  |  |
| 48V DC System |  |  |  |  |
| (a) | Battery |  |  |  |
| 1. | Manufacturer's Name |  |  |  |
| 2. | Country of Manufacture |  |  |  |
| 3. | Place of Testing |  |  |  |
| 4. | Applicable Standard - IEC |  | 60623 |  |
| 5. | Manufacturer’s type designation, and type ref or model number |  | NiCd |  |
| 6. | Voltage | V DC | 48 |  |
| 7. | Capacity at 10-hour rate | Ah | 200 |  |
| 8. | Number of cells |  |  |  |
| 9. | Voltage per cell | V |  |  |
| 10. | Battery voltage at end of the duty cycle | V |  |  |
| 11. | Normal charging rate | A |  |  |
| 12. | Maximum charging rate | A |  |  |
| 13. | Ampere-hour efficiency at ten-hour rate | % |  |  |
| 14. | Ampere-hour efficiency at one hour rate | % |  |  |
| 15. | Dimensions of cells | mm |  |  |
| 16. | Dimensions of battery complete | mm |  |  |
| 17. | Weight of cell complete with electrolyte | kg |  |  |
| 18. | Total weight of battery complete | kg |  |  |
| 19. | Internal resistance per cell when fully charged | ohms |  |  |
| 20. | Material of battery case |  |  |  |
| (b) | Battery Charger |  |  |  |
| 1. | Manufacturer’s name |  |  |  |
| 2. | Manufacturer’s address |  |  |  |
| 3. | Place of Testing |  |  |  |
|  | Type |  | NiCd |  |
| 4. | Manufacturer’s type designation and type ref number or model number |  |  |  |
| 5. | Applied standard |  |  |  |
| 6. | Number of phases | Three | 3 |  |
| 7. | Type of charger control | Micro processor |  |  |
| 8. | AC Input Nominal Voltage | V | 400 |  |
| 9. | AC Input Voltage range | % |  |  |
| 10. | Operating frequency | Hz |  |  |
| 11. | AC input to charger at full load | kVA |  |  |
| 12. | AC input current | A |  |  |
| 13. | DC Nominal Voltage | V | 48 |  |
| 14. | DC output of the charger | kW |  |  |
| 15. | Constant voltage |  |  |  |
|  | (i) Floating charge | V |  |  |
|  | (ii) Equalizing charge | V |  |  |
| 16. | Maximum output voltage |  |  |  |
|  | (i) at automatic control | V |  |  |
|  | (ii) at Boost charge | V |  |  |
| 17. | Regulation | % |  |  |
| 18. | Range of DC voltage control |  |  |  |
| 19. | Output voltage ripple | % | 4 |  |
| 20. | Protection class |  | IP 51 |  |
| 21. | Operating ambient temperature | °C | 45 |  |
| 22. | Dimension |  |  |  |
|  | (i) Height | mm |  |  |
|  | (ii) Width | mm |  |  |
|  | (iii) Depth | mm |  |  |
| 23. | Normal and Boost charge are Independent Units | Yes/No |  |  |
| 24. | Test report reference No: |  |  |  |
| (c) | 48V D.C. Switchboards |  |  |  |
| 1. | Manufacturer's Name |  |  |  |
| 2. | Manufacturer's Address |  |  |  |
| 3. | Place of Testing |  |  |  |
| 4. | Type of construction |  |  |  |
| 5. | Manufacturer’s type designation and type ref number |  |  |  |
| 6. | Busbars: |  |  |  |
|  | (i) Maximum current rating | A |  |  |
|  | (ii) Dimensions | mm |  |  |
| 7. | Boost charge contactors: - |  |  |  |
|  | (i) Manufacturer |  |  |  |
|  | (ii) Maximum current rating | A |  |  |
|  | (iii) Coil rating | W |  |  |
|  | (iv) Method of interlocking |  |  |  |
| 8. | Alarm relays: - |  |  |  |
|  | (i) Manufacturer |  |  |  |
|  | (ii) Type and reference |  |  |  |
|  | (iii) Power consumption: - |  |  |  |
|  | a) Quiescent | A |  |  |
|  | b) Operated | mA |  |  |
| 9. | Number and rating of distribution circuits |  |  |  |
| 10. | Overall dimensions | mm |  |  |
| 11. | Total weight | kg |  |  |

145 KV PROTECTION EQUIPMENT

| No. | Item | Units | Required | Tendered |
| --- | --- | --- | --- | --- |
| 132/11 kV Transformer Biased Differential Protection |  |  |  |  |
| 1. | Manufacturer’s Name and Address |  |  |  |
| 2. | Manufacturer's type designation & model number |  |  |  |
| 3. | Range of operating coil settings | % of CT rating |  |  |
| 4. | Range of bias coil settings | % of CT rating |  |  |
| 5. | 2nd harmonics restraint | Yes/No | Yes |  |
| 6. | High set differential element | Yes/No |  |  |
| 7. | Minimum sensitivity |  |  |  |
|  | - Earth faults | % of CT rating |  |  |
|  | - Phase faults | % of CT rating |  |  |
| 8. | Maximum through fault at which the protective equipment is stable with recommended settings |  |  |  |
|  | - Earth faults | % of CT rating |  |  |
|  | - Phase faults | % of CT rating |  |  |
| 9. | Operating time of relay by twice of setting current | ms |  |  |
| 10. | Test plugs given as per Technical Specification | Yes/No | Yes |  |
| Transformer Restricted Earth Fault Protection |  |  |  |  |
| 1. | Manufacturer's Name & Address |  |  |  |
| 2. | Manufacturer’s type designation & model number |  |  |  |
| 3. | Operating principle, high/low impedance |  | Low impedance |  |
| 4. | Minimum relay setting | A |  |  |
| 5. | Sensitivity of scheme (Allowing for CT magnetizing current, etc.) | A |  |  |
| 6. | Maximum through fault current at which protection is stable. | A |  |  |
| 7. | CT requirements. |  |  |  |
| 8. | Operating time at twice relay minimum setting. | ms |  |  |
| 9. | Operating time at ten times relay minimum setting. | ms |  |  |
| Busbar Protection |  |  |  |  |
| 1. | Manufacturer's Name & Address |  |  |  |
| 2. | Manufacturer’s type designation & model number. |  |  |  |
| 3. | Operating principle, e.g., high impedance, low impedance |  | Low impedance |  |
| 4. | Minimum relay setting |  |  |  |
| 5. | Sensitivity of scheme (Allowing for CT magnetizing current, etc.) |  |  |  |
| 6. | Maximum through fault current at which protection is stable | A |  |  |
| 7. | CT requirements |  |  |  |
| 8. | Estimated magnetizing current at relay setting |  |  |  |
| 9. | Operating time at twice relay minimum setting | ms |  |  |
| 10. | Operating time at ten times relay minimum setting | ms |  |  |
| 11. | Maximum No of input to the relay |  |  |  |
| 12. | Burden per relay input | VA |  |  |
| Tripping Relays |  |  |  |  |
| 1. | Manufacturer's Name & Address |  |  |  |
| 2. | Manufacturer’s type designation and model number |  |  |  |
| 3. | Nominal operating voltage | V |  |  |
| 4. | Minimum operating voltage | V |  |  |
| 5. | Operating indicator |  |  |  |
| 6. | Operating time at nominal voltage | ms |  |  |
| 7. | Contact rating: |  |  |  |
|  | Make and carry continuously | V/A |  |  |
|  | Break resistive watts inductive | VA |  |  |
| Inverse Time Overcurrent and Earth Fault Protection |  |  |  |  |
| 1. | Manufacturer's Name & Address |  |  |  |
| 2. | Manufacturer’s type designation & model number |  |  |  |
| 3. | Inverse time element |  |  |  |
|  | -Standard Inverse | Selectable / Fixed |  |  |
|  | -Very Inverse | Selectable / Fixed |  |  |
|  | -Extremely Inverse | Selectable / Fixed |  |  |
| 4. | Range of current settings: |  |  |  |
|  | (i) over current | A |  |  |
|  | (ii) earth fault | A |  |  |
| 5. | Range of operating times at highest timing setting at ten times current setting | s |  |  |
| 6. | Range of operating times at highest timing setting at twice current setting | s |  |  |
| 7. | High set instantaneous element |  |  |  |
| 8. | Range of settings: |  |  |  |
|  | - over current | A |  |  |
| 9. | Transient over- reach | % |  |  |
| 10. | Operating times: |  |  |  |
|  | - at twice setting | s |  |  |
|  | - at ten times setting | s |  |  |
| 11. | Burden of relay on minimum inverse time element current setting at a current ten times setting |  |  |  |
|  | - overcurrent | VA |  |  |
|  | - earth fault | VA |  |  |
| 12. | Directional element (where applicable) |  |  |  |
| 13. | Operating time |  |  |  |
| 14. | Direction discrimination Minimum voltage required at currents between |  |  |  |
|  | (i) 1 X rated current |  |  |  |
|  | (ii) 10 X rated current |  |  |  |
| 15. | Whether directional element controls the overcurrent protection |  |  |  |
| 16. | Reset time after removal of ten times CT rated current for |  |  |  |
|  | (i) phase element (100%) | ms |  |  |
|  | (ii) EF element (40%) | ms |  |  |
| Line Differential Relay for 132 kV Overhead/Cable Line |  |  |  |  |
| 1. | Manufacturer's Name & Address |  |  |  |
| 2. | Manufacturer’s type designation & model number |  |  |  |
| 3. | Independent measurement per phase | Yes/No |  |  |
| 4. | Integrated backup distance protection | Yes/No | Yes |  |
| 5. | Continuous supervision of protection signal communication | Yes/No | Yes |  |
| 6. | Emergency operation as over current back-up protection | Yes/No | Yes |  |
| 7. | Max. Protection range without add. Transmission device | km |  |  |
| 8. | Max. Protection range with add. Transmission device | km |  |  |
| 9. | Typical operating time | ms |  |  |
| 10. | Restraint criteria |  |  |  |
| 11. | Basic Setting range |  |  |  |
| 12. | Provision for transmitting binary signals | Yes/No | Yes |  |
| Distance Protection for 132kV Overhead Lines / Cable |  |  |  |  |
| 1. | Manufacturer's Name & Address |  |  |  |
| 2. | Manufacturer’s type designation & model number |  |  |  |
| 3 | Integrated into differential element | Yes/No | Yes |  |
| 4. | Segregated Measuring Element for phase to phase and phase to earth fault | Yes/No | Yes |  |
| 5. | Segregated Element for each Zone | Yes/No | Yes |  |
| 6. | Number of zones |  | Min 3 |  |
| 7. | Shape of impedance characteristic |  |  |  |
|  | - Zone 1 |  |  |  |
|  | - Zone 2 |  |  |  |
|  | - Zone 3 |  |  |  |
|  | Reverse looking element (blocking signal initiation) |  |  |  |
| 8. | Sensitivity: |  |  |  |
|  | (i) Minimum operating current | A |  |  |
|  | - Earth faults |  |  |  |
|  | - Phase faults |  |  |  |
|  | (ii) Minimum necessary voltage at Zone 1 reach point (if applicable) | V |  |  |
|  | - Earth faults |  |  |  |
|  | - Phase faults |  |  |  |
|  | (iii) Minimum zone 1 ohmic impedance to which relay can be set | ohms |  |  |
|  | (iv) Maximum zone 1 ohmic impedance to which relay can be set and maintain accuracy | ohms |  |  |
|  | (v) Minimum zone 2 ohmic impedance to which relay can be set | ohms |  |  |
|  | (vi) Maximum zone 2 ohmic impedance to which relay can be set and | ohms |  |  |
|  | (vii) Maximum zone 3 ohmic reach | ohms |  |  |
|  | Forward reach |  |  |  |
|  | Reverse reach |  |  |  |
| 9. | Are forward and reverse reach setting independent of each other? | Yes/No |  |  |
| 10. | Can resistance and reactance reaches be set independent of each other? | Yes/No |  |  |
| 11. | Directional sensitivity | V |  |  |
| 12. | Current transformer requirements |  |  |  |
| 13. | Voltage transformer requirements |  |  |  |
| 14. | Back up zone time ranges | s |  |  |
|  | - Zone 1 |  |  |  |
|  | - Zone 2 |  |  |  |
|  | - Zone 3 |  |  |  |
| 15. | Method used to clear close-in faults |  |  |  |
|  | (i) which occur when line is already energized in service |  |  |  |
|  | (ii) which exist upon line energization |  |  |  |
| Dead Line Check Relays |  |  |  |  |
| 1. | Manufacturer's Name & Address |  |  |  |
| 2. | Manufacturer’s type designation & model number |  |  |  |
| 3. | Voltage setting ranges |  |  |  |
|  | (i) Busbar Voltage | V |  |  |
|  | (ii) Line Voltage | V |  |  |
| 4. | Any time delays (Specify function and value) |  |  |  |
| Synchronising Check Relays |  |  |  |  |
| 1. | Manufacturer's Name & Address |  |  |  |
| 2. | Manufacturer’s type designation |  |  |  |
| 3. | Setting ranges |  |  |  |
|  | (i) Phase angles | degrees |  |  |
|  | (ii) Voltage difference | V |  |  |
|  | (iii) Frequency | Hz |  |  |
| 4. | Any time delays (Specify function and value) |  |  |  |
| Breaker Failure Protection |  |  |  |  |
| 1. | Manufacturer's Name & Address |  |  |  |
| 2. | Manufacturer’s type designation |  |  |  |
| 3. | Setting of current elements: |  |  |  |
|  | (i) phase faults |  |  |  |
|  | (ii) earth faults |  |  |  |
| 4. | Timer setting |  |  |  |
| 5. | Burden of relay at minimum current setting at 10 times CT secondary rated current during: |  |  |  |
|  | (i) phase faults |  |  |  |
|  | (ii) earth faults |  |  |  |
| 6. | Reset time of overcurrent element |  | 15ms or less |  |
| Intercropping Send/Receiver Relays |  |  |  |  |
| 1. | Manufacturer's Name & Address |  |  |  |
| 2. | Manufacturer’s type designations & model number |  |  |  |
|  | (i) send relay |  |  |  |
|  | (ii) receive relay |  |  |  |
| 3. | Send relay: |  |  |  |
|  | (i) Insulation level: kV (minimum 15kV) |  |  |  |
|  | (ii) Rated operating voltage: | V |  |  |
|  | (iii) Operating time at nominal volts: | ms |  |  |
|  | (iv) Is operation indicator fitted: |  |  |  |
|  | (v) Is injection resistor required: |  |  |  |
|  | (vi) Insulation level of injection resistor: |  |  |  |
| 4. | Receive relay: |  |  |  |
|  | (i) Insulation level: kV (minimum 15kV) |  |  |  |
|  | (ii) Degree of surge proofing | Amps a.c.& 50Hz |  |  |
|  | (iii) Minimum operating voltage/current: | V/A |  |  |
|  | (iv) Nominal operating voltage/current | V/A |  |  |
|  | (v) Operating time at nominal operating | ms |  |  |
|  | (vi) Voltage/Current | V/A |  |  |
|  | (vii) Is operation indicator fitted |  |  |  |
| Under Frequency Relay (If Applicable) |  |  |  |  |
| 1. | Manufacturer's Name & Address |  |  |  |
| 2. | Manufacturer’s type designation & model number |  |  |  |
| 3. | Frequency setting range | Hz |  |  |
| 4. | Accuracy |  |  |  |
| 5. | Time delay setting ranges | s |  |  |
| Relay Test Equipment |  |  |  |  |
| 1 | Manufacture | - |  |  |
| 2 | Type | - |  |  |

12 KV PROTECTION EQUIPMENT

| No. | Item |  | Units | Required 12kV | Tendered 12kV |
| --- | --- | --- | --- | --- | --- |
| Transformer Restricted Earth Fault Protection |  |  |  |  |  |
| 1. | Manufacturer's Name & Address |  |  |  |  |
| 2. | Manufacturer’s type designation & model number |  |  |  |  |
| 3. | Operating principle, high impedance |  |  |  |  |
| 4. | Minimum relay setting |  | A |  |  |
| 5. | Sensitivity of scheme (Allowing for CT magnetizing current, etc.) |  | A |  |  |
| 6. | Maximum through fault current at which protection is stable. |  | A |  |  |
| 7. | CT requirements. |  |  |  |  |
| 8. | Operating time at twice relay minimum setting. |  | ms |  |  |
| 9. | Operating time at ten times relay minimum setting. |  | ms |  |  |
| Tripping Relays |  |  |  |  |  |
| 1. | Manufacturer's Name & Address |  |  |  |  |
| 2. | Manufacturer’s type designation and model number |  |  |  |  |
| 3. | Nominal operating voltage |  | V |  |  |
| 4. | Minimum operating voltage |  | V |  |  |
| 5. | Operating indicator |  |  |  |  |
| 6. | Operating time at nominal voltage |  | ms |  |  |
| 7. | Contact rating: |  |  |  |  |
|  | (i) Make and carry continuously |  | V/A |  |  |
|  | (ii) Break resistive watts inductive |  | VA |  |  |
| Inverse Time Overcurrent & Earth Fault Protection |  |  |  |  |  |
| 1. |  | Manufacturer's Name & Address |  |  |  |
| 2. |  | Manufacturer’s type designation & model number |  |  |  |
| 3. |  | Inverse time element |  |  |  |
| 4. |  | Range of current settings: |  |  |  |
|  |  | (i) over current | A |  |  |
|  |  | (ii) earth fault | A |  |  |
| 5. |  | Range of operating times at highest timing setting at ten times current setting | s |  |  |
| 6. |  | Range of operating times at highest timing setting at twice current setting | s |  |  |
| 7. |  | High set instantaneous element |  |  |  |
| 8. |  | Range of settings: |  |  |  |
|  |  | - over current | A |  |  |
| 9. |  | Transient over- reach | % |  |  |
| 10. |  | Operating times: |  |  |  |
|  |  | - at twice setting | s |  |  |
|  |  | - at ten times setting | s |  |  |
| 11. |  | Burden of relay on minimum inverse time element current setting at a current ten times setting |  |  |  |
|  |  | - overcurrent | VA |  |  |
|  |  | - earth fault | VA |  |  |
| 12. |  | Directional element (where applicable) |  |  |  |
| 13. |  | Operating time |  |  |  |
| 14. |  | Direction discrimination Minimum voltage required at currents between |  |  |  |
|  |  | (i) 1 X rated current |  |  |  |
|  |  | (ii) 10 X rated current |  |  |  |
| 15. |  | Whether directional element controls the overcurrent protection |  |  |  |
| 16. |  | Reset time after removal of ten times CT rated current for |  |  |  |
|  |  | (i) phase element (100%) | ms |  |  |
|  |  | (ii) EF element (40%) | ms |  |  |
| Dead Line Check Relays |  |  |  |  |  |
| 1. |  | Manufacturer's Name & Address |  |  |  |
| 2. |  | Manufacturer’s type designation & model number |  |  |  |
| 3. |  | Voltage setting ranges |  |  |  |
|  |  | (i) Busbar voltage | V |  |  |
|  |  | (ii) Line Voltage | V |  |  |
| 4. |  | Any time delays (Specify function and value) |  |  |  |
| Synchronising Check Relays |  |  |  |  |  |
| 1. | Manufacturer's Name & Address |  |  |  |  |
| 2. | Manufacturer’s type designation |  |  |  |  |
| 3. | Setting ranges |  |  |  |  |
|  | (i) Phase angles |  | degrees |  |  |
|  | (ii) Voltage difference |  | V |  |  |
|  | (iii) Frequency |  | Hz |  |  |
| 4. | Any time delays (Specify function and value) |  |  |  |  |
| Under Frequency Relay |  |  |  |  |  |
| 1. | Manufacturer's Name & Address |  |  |  |  |
| 2. | Manufacturer’s type designation & model number |  |  |  |  |
| 3. | Frequency setting range |  | Hz |  |  |
| 4. | Accuracy |  |  |  |  |
| 5. | Time delay setting ranges |  | s |  |  |

SUBSTATION AUTOMATION SYSTEM

| No. | Item | Units | Required | Tendered |
| --- | --- | --- | --- | --- |
| 1. | Manufacturer's Name |  |  |  |
| 2. | Manufacturer’s Country |  |  |  |
| 3. | Manufacturer’s type designation & model number |  |  |  |
| 4. | Temperature range |  |  |  |
|  | a. Operation | °C | -10 to +50 |  |
|  | b. Transport and storage | °C | 10 to +70 |  |
| 5. | Relative humidity |  |  |  |
|  | a. Operation max./min. | % | 95/5 |  |
|  | b. Transport and storage | % | > 95/5 |  |
| 6. | All independent circuits fully galvanically isolated |  | Yes |  |
| 7. | Dielectric strength, AC 50Hz, 1Min. | kV | 2 |  |
| 8. | MTBF of I/O board | h | >100,000 |  |
| 9. | MTBF of CPU board | h | >80,000 |  |
| 10. | MTTR | h | <1 |  |
| 11. | Self-test system |  | Yes |  |
| 12. | Transmission protocol standard |  | IEC 61850 |  |
| 13. | Transmission modes (programmable and by parameter changes) |  | Yes |  |
| 14. | Parallel transmission on two channels and receiving on the best one |  | Yes |  |
| 15. | Parallel transmission on both channels and receiving on both channels |  | Yes |  |
| 16. | Transmitted information chronology |  |  |  |
| 17. | Status changes transmitted with time tag (1ms) |  | Yes |  |

FIBRE OPTIC & SCADA/TELECOMMUNICATION EQUIPMENT

| No. | Item | Units | Required | Tendered |
| --- | --- | --- | --- | --- |
| SDH-Multiplexer (Fibre Optic Equipment) |  |  |  |  |
| (a) | Main Services |  |  |  |
| 1. | Manufacturer's name & address |  |  |  |
| 2. | Manufacturer’s type designation & model number |  |  |  |
| 3. | Standards |  | By tender Specification |  |
| 4. | Working temperature range | °C |  |  |
| 5. | Relative humidity |  |  |  |
| 6. | Working voltage | V DC | -48V DC |  |
| 7. | Power consumption | W |  |  |
| 8. | Size of panel (W x D x H) | mm |  |  |
| (b) | SDH card |  |  |  |
| 1. | Bit Rate | MBits/s |  |  |
| 2. | STM-4 optical interfaces for directions |  |  |  |
| 3. | 1+1 path protection |  | Yes |  |
| 4. | Power Consumption | W |  |  |
| (c) | Other Interface Card |  |  |  |
| (i) | 4wire Voice Interfaces for PLTS |  |  |  |
| 1. | Humidity |  |  |  |
| 2. | Voice Channels per module |  | > 08 |  |
| 3. | Power Consumption | W |  |  |
| (ii) | E1 Interface |  |  |  |
| 1. | Bit Rate | kBits/s |  |  |
| 2. | Options |  | > 08 |  |
| 3. | Number of Interfaces |  |  |  |
| 4. | Power Consumption | W |  |  |
| (iii) | FXS Interface |  |  |  |
| 1. | Input level | dBr |  |  |
| 2. | Output level | dBr |  |  |
| 3. | Frequency Response |  |  |  |
| 4. | Idle Channel Noise |  |  |  |
| 5. | Ring Voltage |  |  |  |
| 6. | Signaling |  |  |  |
| 7. | Voice Channels per module |  | > 10 |  |
| 8. | Power Consumption | W |  |  |
| (iv) | Data Interface (V.24/V.28) |  |  |  |
| 1. | Bit Rate | kBits/s |  |  |
| 2. | Options |  |  |  |
| 3. | Number of Interfaces |  |  |  |
| 4. | Power Consumption | W |  |  |
| (v) | Ethernet Interface for SAS |  |  |  |
| 1. | Bit Rate | MBits/s | 10/100 Base |  |
| 2. | Routing facilities |  | Yes |  |
| 3. | Separate Ethernet Rings |  | Yes |  |
| 4. | Number of Interfaces |  | > 8 |  |
| 5. | Power Consumption | W |  |  |
| (vi) | Tele protection Interface |  |  |  |
| 1. | Voltage Range | V DC |  |  |
| 2. | Output Current (Cont./Surge) | A |  |  |
| 3. | Propagation Delay Time | ms |  |  |
| 4. | 1+1 path Switchover Time | ms |  |  |
| 5. | Number of Interfaces | Nos |  |  |
| 6. | Power Consumption | W |  |  |
| VoIP Telephone System |  |  |  |  |
| (a) | IP Phone |  |  |  |
| 1. | Manufacturer's name & address |  |  |  |
| 2. | Manufacturer’s type designation & model number |  |  |  |
| 3. | Standards |  | By tender Specification |  |
| 4. | Working temperature range | °C |  |  |
| 5. | Relative humidity |  |  |  |
| 6. | Working voltage | V DC | -48V DC |  |
| 7. | Power consumption | W |  |  |
| 8. | Size of panel (W x D x H) | mm |  |  |

GROUNDING MATERIALS

| No. | Item | Units | Required | Tendered |
| --- | --- | --- | --- | --- |
| (a) | Shield Wire System |  |  |  |
| 1. | Manufacturer’s name and address |  |  |  |
| 2. | Material |  |  |  |
| 3. | Overall diameter | mm |  |  |
| 4. | Nominal section | mm2 |  |  |
| 5. | Cross section and make-up |  |  |  |
| 6. | Maximum rated current (3 Sec.) | A |  |  |
| 7. | Maximum working tension of main connections | kg/m2 |  |  |
| 8. | Resistance of conductor per 100 m at 30 0C | ohm |  |  |
| 9. | Tensile breaking stress of material | N/mm2 |  |  |
| 10. | Maximum permissible span length | m |  |  |
| 11. | Maximum sag under own weight of maximum span | mm |  |  |
| (b) | Earthing Grid |  |  |  |
| 1. | Manufacturer’s name and address |  |  |  |
| 2. | Material |  |  |  |
| 3. | Overall diameter | mm |  |  |
| 4. | Nominal section | mm2 |  |  |
| 5. | Maximum rated current (3 Sec) | A |  |  |
| 6. | Resistance of conductor per 100 m at 30 0C | ohm |  |  |
| (c) | Grounding Electrodes |  |  |  |
| 1. | Manufacturer’s name and address |  |  |  |
| 2. | Material |  |  |  |
| 3. | Dimensions |  |  |  |
| 4. | Number of electrodes per group |  |  |  |
| 5. | Number of earthing points per substation |  |  |  |
| 6. | Calculated resistance of combined earth grid and points |  |  |  |

CABLES

| No. |  | Item | Units | Required | Tendered |
| --- | --- | --- | --- | --- | --- |
| 1000V Cables（If Applicable） |  |  |  |  |  |
| 1. |  | Identification nos. |  |  |  |
| 2. |  | Manufacturers name and address |  |  |  |
| 3. |  | Number of cores |  |  |  |
| 4. |  | Cross sectional area | mm² |  |  |
| 5. |  | Core stranding |  |  |  |
|  |  | - Number |  |  |  |
|  |  | - Diameter | mm |  |  |
| 6. |  | Insulation thickness | mm |  |  |
| 7. |  | Materials of insulation |  |  |  |
| 8. |  | Type of filler |  |  |  |
| 9. |  | Type of tape |  |  |  |
| 10. |  | Bedding thickness | mm |  |  |
| 11. |  | Bedding outer diameter | mm |  |  |
| 12. |  | Type of sheath | mm |  |  |
| 13. |  | Sheath thickness | mm |  |  |
| 14. |  | Completed cable |  |  |  |
|  |  | - Diameter | mm |  |  |
|  |  | - Weight per meter | kg |  |  |
|  |  | - Max. drum length | m |  |  |
| 15. |  | Minimum installed bending radius | mm |  |  |
| 16. |  | Maximum conductor temperature | °C |  |  |
| 17. |  | Maximum DC resistance of conductor per km of cable at 20 °C | ohm |  |  |
| Multicore Control Cables |  |  |  |  |  |
|  |  | Items Nos: (List types) |  |  |  |
| 1. |  | Identification nos. |  |  |  |
| 2. |  | Manufacturers name & address |  |  |  |
| 3. |  | Number of cores |  |  |  |
| 4. |  | Cross section area | mm2 |  |  |
| 5. |  | Core stranding |  |  |  |
|  |  | (i) Number |  |  |  |
|  |  | (ii) Diameter | mm |  |  |
| 6. |  | Insulation thickness | mm |  |  |
| 7. |  | Materials of insulation |  |  |  |
| 8. |  | Type of filter |  |  |  |
| 9. |  | Type of tape |  |  |  |
| 10. |  | Bedding thickness | mm |  |  |
| 11. |  | Bedding outer diameter | mm |  |  |
| 12. |  | Type of sheath | mm |  |  |
| 13. |  | Sheath thickness | mm |  |  |
| 14. |  | Completed cable: |  |  |  |
|  |  | (i) Diameter | mm |  |  |
|  |  | (ii) Weight per meter | kg |  |  |
|  |  | (iii) Max. drum length | m |  |  |
| 15. |  | Minimum installed bending radius | mm |  |  |
| 16. |  | Maximum conductor temperature | °C |  |  |
| 17. |  | Maximum DC resistance of conductor per km of cable at 20 0C | ohm |  |  |
| 132 kV Single Core XLPE Cable |  |  |  |  |  |
| 5.1 |  | General |  |  |  |
|  |  | - Name of manufacturer | - |  |  |
|  |  | - Location of manufacturing site | - |  |  |
|  |  | Manufacturer’s Quality Certification |  | ISO 9001 or equivalent |  |
|  |  | - Name of Certifying authority | - |  |  |
|  |  | - Validity of Certificate (year) | - |  |  |
|  |  | - Required Power Transmission Capacity of 400mm2 Cable | MVA | 30 |  |
|  |  | General description of 132kV cable |  |  |  |
|  |  | a. Number of cores | - | Single core |  |
|  |  | b. Maximum rated Voltage (Um) | kV | 145 |  |
|  |  | c. Conductor cross section | mm2 |  |  |
|  |  | d. Insulation Type | - | XLPE |  |
|  |  | e. Type of over-sheath | - | HDPE/PVC |  |
|  |  | - Year of first commercial operation of cable type | - |  |  |
| 5.2 |  | Insulation Rating |  |  |  |
|  |  | - Maximum Rated voltage, phase to phase (Um) | kV | 145 |  |
|  |  | - Nominal operating voltage, phase to phase (U) | kV | 132 |  |
|  |  | - Nominal operating voltage, phase to earth (U0) | kV | 76 |  |
|  |  | - Rated frequency | Hz | 50 |  |
|  |  | - Rated impulse withstand voltage (Upeak) | kV | 650 |  |
|  |  | - Rated Short time Power frequency withstand voltage | kV /30min | 190 |  |
| 5.3 |  | Conductor |  |  |  |
|  |  | - Material | - | Copper |  |
|  |  | - Nominal cross-section | mm2 |  |  |
|  |  | - Shape and type of Conductor | - | Milliken (stranded and segmented) |  |
|  |  | - Number of segments |  | 4 or more |  |
|  |  | - Water blocking method |  | Swelling powder or tapes |  |
|  |  | - Semi-conducting binder tape |  |  |  |
| 5.4 |  | Conductor screen (inner shielding layer) |  |  |  |
|  |  | - Type of Material | - | Semi-con., XLPE, fully bonded to the insulation |  |
|  |  | - Visible irregularities on outer surface | m | 76 |  |
|  |  | - Maximum void at the interface between conductor screen and insulation | m | 51 |  |
|  |  | - Production method |  | Extrusion |  |
|  |  | - Volume Resistivity | Ohm-m | 1000 |  |
|  |  | Wall thickness |  |  |  |
|  |  | - Average value | mm |  |  |
|  |  | - Minimum value | mm | 0.76 |  |
| 5.5 |  | Insulation |  |  |  |
|  |  | - Material | - | XLPE |  |
|  |  | - Maximum void in the insulation | m | 51 |  |
|  |  | - Number of voids larger than 0.025mm per cubic centimeter |  | 1.8 |  |
|  |  | - Maximum contaminant in the insulation | mm | 0.127 |  |
|  |  | - Number of contaminants between 0.051 to 0.127mm per cubic centimeter in the insulation |  | 0.6 |  |
|  |  | - Maximum amber in the insulation | mm | 0.254 |  |
|  |  | Maximum stress at nominal voltage as per |  | ICEA S-108- 720-2012 |  |
|  |  | a. At conductor screen | kV/mm | ≤8 |  |
|  |  | b. At insulation screen | kV/mm | ≤4 |  |
|  |  | Maximum stress at impulse voltage as per |  | ICEA S-108- 720-2012 |  |
|  |  | a. At conductor screen | kV/mm |  |  |
|  |  | b. At insulation screen | kV/mm |  |  |
|  |  | - Nominal thickness | mm |  |  |
|  |  | - Minimum thickness | mm |  |  |
|  |  | - Maximum partial discharge | pC | no detectable exceeding the sensitivity |  |
|  |  | - Maximum losses/tan delta | - | ≤10×10-4 |  |
|  |  | - Minimum tensile strength | N/mm2 | 12.5 |  |
| 5.6 |  | Insulation screen (outer shielding layer) |  |  |  |
|  |  | - Type of Material | - | Fully bonded semi- con. XLPE |  |
|  |  | - Visible irregularities at the interface between insulation and insulation screen | µm | 127 |  |
|  |  | - Maximum void at the interface between insulation and insulation screen | m | 51 |  |
|  |  | - Resistivity | Ohm-m | 500 |  |
|  |  | Wall thickness – minimum & maximum value | mm | ≤1.02~≤2.54 |  |
| 5.7 |  | XLPE manufacturing Method |  |  |  |
|  |  | - Extrusion line type | - | VCV |  |
|  |  | - Single pass triple extrusion | - |  |  |
|  |  | - Curing method | - | Dry |  |
|  |  | - Cooling method | - | Dry |  |
| 5.8 |  | Water barrier |  |  |  |
|  |  | - Type & material | - | Semi-con swellable tape |  |
|  |  | - Nominal thickness |  |  |  |
| 5.9 |  | Bedding |  |  |  |
|  |  | - Type and material | - | Semi-con swellable tape |  |
|  |  | - Nominal thickness |  |  |  |
| 5.10 |  | Metallic screen |  |  |  |
|  |  | - Type & Material | - | Copper wire & / or tape |  |
|  |  | - Wire diameter & numbers |  |  |  |
|  |  | a. Outer phase cables | mm/nos. |  |  |
|  |  | b. Center phase cable | mm/nos. |  |  |
|  |  | - Total cross-sectional area |  |  |  |
|  |  | a. Outer phase cables | mm/nos. |  |  |
|  |  | b. Center phase cable | mm/nos. |  |  |
|  |  | - Nominal thickness of copper tape, if any | mm |  |  |
|  |  | - Cross sectional area of screen | mm2 |  |  |
|  |  | - Earth fault current (1 sec) combination with Metallic Sheath (Lead alloy) | kA | 40 |  |
| 5.11 |  | Binder |  |  |  |
|  |  | - Material | - | Semi-con swellable tape(s) |  |
|  |  | - Number of tapes and thickness | - |  |  |
| 5.12 |  | Outer sheath (protective layer) |  |  |  |
|  |  | - Material | - | HDPE/PVC |  |
|  |  | - Nominal wall thickness | mm | 6.0 |  |
|  |  | - Color | - | black |  |
|  |  | - Tensile strength without aging | N/mm2 | 12.5 |  |
|  |  | - Termite resistance |  |  |  |
| 5.13 |  | Type of conductive outer layer | - | Graphite layer |  |
| 5.14 |  | Nominal Overall cable diameter | - |  |  |
| 5.15 |  | Weight of completed cable |  |  |  |
|  |  | - Copper | Kg/m |  |  |
|  |  | - Lead Alloy | Kg/m |  |  |
|  |  | - Gross weight | Kg/m |  |  |
| 5.16 |  | Transmission capacity of 132kV / single core XLPE cable | MVA | 30 |  |
| 5.17 |  | Reactive power requirements |  |  |  |
|  |  | - Maximum charging current | A/km |  |  |
| 5.18 |  | Short circuit currents |  |  |  |
|  |  | - Max three phase short circuit current for 3 sec | kA | 40 |  |
|  |  | - Max earth fault current for 1sec | kA | 40 |  |
|  |  | - Max conductor temperature for three phase/earth fault 40kA, 3 sec. | °C | 250 |  |
| 5.19 |  | Electrical Parameters |  |  |  |
|  |  | - Copper purity |  | 99.99% |  |
|  |  | - Nominal resistance | Ohm/km |  |  |
|  |  | - Maximum DC resistance of conductor at 20 °C | Ohm/km | 0.0151 |  |
|  |  | - AC resistance of conductor at 20 °C | Ohm/km |  |  |
|  |  | - AC resistance of conductor at 90 °C | Ohm/km |  |  |
|  |  | - DC resistance of metal sheath at 20 °C | Ohm/km |  |  |
|  |  | - DC resistance of copper wire screen at 20 °C | Ohm/km |  |  |
|  |  | - Max field strength at conductor screen at U0=76 kV | kV/mm |  |  |
|  |  | - Charging current per phase at operating voltage | A/km |  |  |
|  |  | - Charging power per circuit at operating voltage | kVar/km |  |  |
|  |  | - Dielectric loss factor at 20/90 °C | p.u. | ≤10×10-4 |  |
|  |  | - Service capacitance | µF/km |  |  |
|  |  | - Inductance for flat formation (400 mm between phases) |  |  |  |
|  |  | - Phase L1 | mH/km |  |  |
|  |  | - Phase L2 | mH/km |  |  |
|  |  | - Phase L3 | mH/km |  |  |
|  |  | - Reactance for flat formation (400 mm between phases) |  |  |  |
|  |  | - Phase L1 | Ohm/km |  |  |
|  |  | - Phase L2 | Ohm/km |  |  |
|  |  | - Phase L3 | Ohm/km |  |  |
|  |  | - Surge impedance of cable | Ohm |  |  |
|  |  | - Max positive sequence & negative sequence impedance |  |  |  |
|  |  | (1) with sheath current | Ohm/km |  |  |
|  |  | (2) without sheath current | Ohm/km |  |  |
|  |  | - Max zero sequence impedance (return currents in sheath) | Ohm/km |  |  |
| 5.20 |  | Current ratings | mm2 |  |  |
|  |  | - Max permissible continuous current carrying capacity per circuit 30 MVA; |  |  |  |
|  |  | - A1 option specified trench, trefoil formation | A |  |  |
|  |  | - A2 option laid in air, 40 °C air temperature, flat formation., 400 mm spacing | A |  |  |
|  |  | - A4 option laid in 250mmØ HDPE pipes, Trefoil formation, in air | A |  |  |
|  |  | Current Carrying Capacity at Emergency Conditions |  |  |  |
|  |  | Calculate the Emergency Current level that can be carried for max. 4 hours without exceeding the maximum operating temperature 90 °C, assuming that the cable system is operating at required rated current (30 MVA). |  |  |  |
|  |  | a. For 1 hour | A |  |  |
|  |  | b. For 2 hours | A |  |  |
|  |  | c. For 3 hours | A |  |  |
|  |  | d. For 4 hours | A |  |  |
|  |  | - System load factor |  | 0.8 |  |
| 5.21 |  | Cable losses |  |  |  |
|  |  | - Max continuous current, cross-bonding, nominal voltage, 40 °C, |  |  |  |
|  |  | (1) Conductor | kW/km |  |  |
|  |  | (2) Dielectric | kW/km |  |  |
|  |  | (3) Metal sheath | kW/km |  |  |
|  |  | (4) Copper wire screen | kW/km |  |  |
|  |  | (5) Total losses at rated capacity (total of 1,2,3 and 4) | kW/km |  |  |
| 5.22 |  | Mechanical data and dimension of cable |  |  |  |
|  |  | - Outer diameter | mm |  |  |
|  |  | - Net weight | kg/km |  |  |
|  |  | - Max delivery length (according to site conditions) | m |  |  |
|  |  | - Min. permissible bending radius (according to site conditions) | m |  |  |
|  |  | - Max. permitted pulling tension | kN |  |  |
|  |  | - Transport dimensions of cable drum shall comply with Sri Lanka transport regulations of weight and height |  |  |  |
| Accessories of 132 kV Single Core XLPE Cable |  |  |  |  |  |
| 6.1 | 132 kV Cable joints |  |  |  |  |
|  | - Manufacturer |  | - |  |  |
|  | - Location of manufacturing site |  | - |  |  |
|  | - Manufacturing & test Standard |  | - | IEC 60840 |  |
|  | - Type of Joint |  | - | pre-moulded |  |
|  | Manufacturer’s Quality Certification |  |  | ISO 9001 or equivalent |  |
|  | - Name of Certifying authority |  | - |  |  |
|  | - Validity of Certificate (year) |  | - |  |  |
|  | Joint (Straight through) |  | - |  |  |
|  | - Conductor jointing method |  | - |  |  |
|  | - Joint sleeve (shell) |  |  | Copper with lead plumb seals |  |
|  | - Requirement of joint box enclosure |  | - | Watertight |  |
|  | - Overall diameter |  | mm |  |  |
|  | - Overall length |  | mm |  |  |
|  | Joint (Sheath sectionalize) |  |  |  |  |
|  | - Conductor jointing method |  | - |  |  |
|  | - Joint sleeve (shell) |  | - | Copper with lead plumb seals |  |
|  | - Requirement of joint box enclosure |  | - | Watertight |  |
|  | - Overall diameter |  | mm |  |  |
|  | - Overall length |  | mm |  |  |
|  | Electrical Data |  |  |  |  |
|  | - Nominal operating voltage (U0) |  | kV | 76 |  |
|  | - Nominal operating voltage (U) |  | kV | 132 |  |
|  | - Rated voltage (Um) |  | kV | 145 |  |
|  | - Lighting impulse withstand voltage (peak) |  | kV | 650 |  |
|  | - Power frequency withstand voltage |  | kV/30min | 190 |  |
|  | - Max. dielectric stress as per |  | kV/mm | ICEA S-108- 720-2012 |  |
|  | Requirement of Joint design |  |  |  |  |
|  | - Joint Components |  | - | Pre-fabricated |  |
|  | Requirement of Type test report |  |  |  |  |
|  | - Name of Independent test authority |  | - |  |  |
|  | - Standard for type test |  | - | IEC 60840 |  |
| 6.2 | 132kV Cable Termination for GIS |  |  |  |  |
|  | - Manufacturer |  |  |  |  |
|  | - Location of manufacturing site |  |  |  |  |
|  | - Manufacturing & test Standard |  |  | IEC 60840 |  |
|  | - Termination Type |  |  | Stress relief cone |  |
|  | Manufacturer’s Quality Certification |  |  |  |  |
|  | - Certified by (Company name) |  | - |  |  |
|  | - Certification validity till (year) |  | - |  |  |
|  | Electrical Data |  |  |  |  |
|  | - Nominal operating voltage (U0) |  | kV | 76 |  |
|  | - Nominal operating voltage (U) |  | kV | 132 |  |
|  | - Highest system voltage (Um) |  | kV | 145 |  |
|  | - Lighting impulse withstand voltage (peak) |  | kV | 650 |  |
|  | - Power frequency withstand voltage |  | kV/30min | 190 |  |
|  | - max dielectric stress |  | kV/mm | ≤cable requirement |  |
|  | - Type test report |  | - |  |  |
|  | - Type test standard |  | - | IEC 60840 |  |
| 6.3 | Surge Voltage Limiters (SVL) |  |  |  |  |
|  | - Name of Manufacturer |  | - |  |  |
|  | - Location of manufacturing site |  | - |  |  |
|  | - Type of SVL |  | - | ZnO nonlinear |  |
|  | Requirement of Type test |  | - |  |  |
|  | - Name of Independent testing authority |  | - |  |  |
|  | - Date of type test certificate |  | - |  |  |
|  | - Standard for type test |  |  | IEC 60840 |  |
|  | Characteristic of SVL |  |  |  |  |
|  | - SVL protective level |  | kV | min. 6 |  |
|  | - Residual Voltage @ 10 kA, 8×20µSec wave |  | kV |  |  |
|  | - Operating Voltage with test current 1mA (D.C) |  | kV | 5 |  |
|  | - Surge capability at 8×20µSec wave |  | kA | ≥15 |  |
|  | - Fault current withstand |  | Sec | min 3 |  |
|  | - Energy absorption |  | kW | ≥10 |  |
|  | - Insulation resistance at 1000V d.c. voltage |  | M-ohm | ≥2 |  |
|  | - Permissible ambient temperature |  | °C | 50 |  |
|  | Nominal physical dimensions |  |  |  |  |
|  | - Diameter |  | mm |  |  |
|  | - Height |  | mm |  |  |
| 6.4 | Link boxes |  | - |  |  |
|  | - Name of Manufacturer |  | - |  |  |
|  | - Location of manufacturing site |  | - |  |  |
|  | Type designation |  | - |  |  |
|  | - With SVL |  | - |  |  |
|  | - For solid earthing |  | - |  |  |
|  | Requirement of Type test |  |  |  |  |
|  | - Along the route |  |  | Lockable/ buried |  |
|  | - At terminal location |  |  | Lockable/ wall mounted |  |
|  | Requirement of Type test |  |  |  |  |
|  | - Name of the Independent testing laboratory |  | - |  |  |
|  | - Date of type test certificate |  | - |  |  |
|  | Link Box casing |  |  |  |  |
|  | - Type of material |  |  | Cast iron |  |
|  | - Requirement for waterproof test |  | - | min. height of water level 1 m |  |
|  | - D.C. Voltage test, 1minute |  | kV | 10 |  |
|  | Link Box dimensions |  |  |  |  |
|  | - Width |  | mm |  |  |
|  | - length |  | mm |  |  |
|  | - Height |  | mm |  |  |
|  | - Protection Class (IP code) |  |  | IP68 |  |
| 6.5 | Earthing Cable |  |  |  |  |
|  | - Name Manufacturer |  | - |  |  |
|  | - Type & material of cable |  | - | Concentric/ Stranded copper |  |
|  | - Manufacturing & testing Standard |  | - | IEC 60502-1 |  |
|  | - Nominal Cross-section of conductor |  | mm2 |  |  |
|  | - No. of wires/ Diameter |  | Nos./mm |  |  |
|  | - Thickness of extruded PVC covering |  | mm |  |  |
|  | - Maximum earth fault current for 1 sec. |  | kA | 40 |  |
| 11 kV Single Core XLPE Cable |  |  |  |  |  |
| 9.1 | Insulation strength |  |  |  |  |
|  | - Nominal operating voltage, phase to earth, U0 |  | kV | 6.35 |  |
|  | - Nominal operating voltage, phase to phase, U |  | kV | 11 |  |
|  | - Rated Voltage - phase to phase Um |  | kV | 12 |  |
|  | - Rated impulse withstand voltage (Upeak) |  | kV | 75 |  |
|  | - Power frequency withstand voltage (1 minutes) |  | kV | 28 |  |
| 9.2 | Conductor |  |  |  |  |
|  | - Material |  | - | Plain Copper |  |
|  | - Nominal cross-section |  | mm2 |  |  |
|  | - Shape and type of conductor |  | - | Stranded Circular Compacted (IEC 60228) |  |
|  | - Number of wires/ diameters |  | No./mm |  |  |
| 9.3 | Conductor screen (inner shielding layer) |  |  |  |  |
|  | - Type of Material |  | - | Semi-con XLPE fully bonded to the insulation |  |
|  | - Method of Production |  |  | Extrusion |  |
|  | - Resistivity |  | Ohm-m | 1000 |  |
|  | - Wall thickness |  |  |  |  |
|  | - Average value |  | mm |  |  |
|  | - Minimum value |  | mm |  |  |
| 9.4 | Insulation |  |  |  |  |
|  | - Material |  | - | XLPE |  |
|  | - Thickness of insulation |  |  | As per IEC 60502-2 |  |
|  | - Average thickness |  | mm |  |  |
|  | - Minimum thickness |  | mm |  |  |
|  | - Maximum dielectric stress at conductor screen |  | kV/mm |  |  |
|  | - Maximum dielectric stress at insulation screen |  | kV/mm |  |  |
|  | - Maximum visible irregularities |  | m |  |  |
|  | - Maximum partial discharge |  | pC |  |  |
|  | - Thermal resistivity according to IEC |  | K*m/W |  |  |
|  | - Max losses/tan delta |  |  |  |  |
| 9.5 | Insulation screen (outer shielding layer) |  |  |  |  |
|  | - Type of Material |  |  | Bonded semi- con XLPE, Cold strippable |  |
|  | - Resistivity |  | Ohm/m | ≤500 |  |
|  | - Method of Production |  | - | Extrusion |  |
|  | - Average wall thickness |  | mm |  |  |
|  | - Visible irregularities |  | m |  |  |
| 9.6 | Metallic (Copper wire) screen |  |  |  |  |
|  | - Type & Material |  | - | Copper wire & tape |  |
|  | - No. of wires & diameter |  | Nos./mm |  |  |
|  | - Nominal cross-section |  | mm2 |  |  |
|  | - Earth fault current (1sec.) combination with Metal Sheath (Lead cover) |  | kA | 25 |  |
| 9.7 | Water barriers |  | - |  |  |
|  | - Type & Material |  | - | Semi-con swellable tape |  |
|  | - Nominal Thickness |  | - |  |  |
|  | - Water tightness (pressure withstand) |  | - | 1m water level |  |
| 9.8 | Fault current Capacity of Copper wire screen |  | kA, per 1 sec | 25 |  |
| 9.9 | Outer sheath (protective layer) |  |  |  |  |
|  | - Protective under coat layer |  |  | Bitumen |  |
|  | - Material |  | - | HDPE/PVC |  |
|  | - Max/min wall thickness |  | mm |  |  |
|  | - Nominal wall thickness |  | mm | 3.5 (IEC 60502-2) |  |
|  | - Thermal resistivity |  | K*m/W |  |  |
|  | - Color |  | - | Black |  |
| 9.10 | Short circuit currents |  |  |  |  |
|  | - Maximum three phase short circuit current between conductors for 3 seconds |  | kA | 25 |  |
|  | - Max conductor temperature for three phase/earth fault |  | °C |  |  |
|  | - Max earth fault current between phase and metallic screen for 1second |  | kA | 20 |  |
|  | - Max permissible short circuit currents of cable (pre-fault conditions: max permissible conductor temperature 90 °C) |  |  |  |  |
|  | (1) for conductor (three phase fault current,3sec) |  | kA |  |  |
|  | (2) for screen & metal sheath (0.5sec) |  | kA |  |  |
|  | (3) for screen & metal sheath (1.0sec) |  | kA |  |  |
|  | (4) for screen &metal sheath (3.0sec) |  | kA |  |  |
| 9.11 | Electrical Parameters |  |  |  |  |
|  | - Copper purity |  |  | 99.99% |  |
|  | - Nominal resistance |  | Ohm/km |  |  |
|  | - DC resistance of conductor at 20 °C |  | Ohm/km | 0.0470 |  |
|  | - AC resistance of conductor at 20 °C |  | Ohm/km |  |  |
|  | - AC resistance of conductor at 90 °C |  | Ohm/km |  |  |
|  | - DC resistance of conductor of metal sheath at 20 °C |  | Ohm/km |  |  |
|  | - DC resistance of conductor of copper wire screen at 20 °C |  | Ohm/km |  |  |
|  | - Inductance for trefoil formation |  |  |  |  |
|  | - Phase L1 |  | mH/km |  |  |
|  | - Phase L2 |  | mH/km |  |  |
|  | - Phase L3 |  | mH/km |  |  |
|  | - Reactance for trefoil formation |  |  |  |  |
|  | - Phase L1 |  | Ohm/km |  |  |
|  | - Phase L2 |  | Ohm/km |  |  |
|  | - Phase L3 |  | Ohm/km |  |  |
| 9.12 | Current ratings |  |  |  |  |
|  | - Max permissible continuous current carrying capacity with trefoil formation under following conditions. - Ambient Temp 40 °C, Ground Temp 30 °C, Depth of laying 800mm, soil thermal resistivity 1.2 °C m/W &-max. Conductor operating temp. 90 °C, both ends solidly bonded & earthed. |  |  |  |  |
|  | (1) Direct in ground |  | A |  |  |
|  | (2) Option1: laid in 100mm Dia PVC ducts |  | A |  |  |
|  | (3) Option2: number of parallel 3 ph. circuits -5 |  | A |  |  |
| 9.13 | Mechanical data and dimension of cable |  |  |  |  |
|  | - Outer diameter |  | mm |  |  |
|  | - Net weight |  | kg/km |  |  |
|  | - Max delivery length (according to site conditions) |  | m |  |  |
|  | - Min. permissible bending radius (according to site conditions) |  | m |  |  |
|  | - Max. permitted pulling tension |  | kN |  |  |
|  | - Transport dimensions of cable drum shall comply with Sri Lanka transport regulations of weight and height |  |  |  |  |
| Accessories of 11 kV Single Core 240mm2 XLPE Cable |  |  |  |  |  |
| 10.1 | 11 kV Cable joints |  |  |  |  |
|  | - Name of Manufacturer |  | - |  |  |
|  | - Location of manufacturing sites |  | - |  |  |
|  | - Manufacturing & Test standards |  | - | IEC 60502-4 |  |
|  | - Nominal operating voltage (phase to earth U0) |  | KV | 6.35 |  |
|  | - Nominal voltage (phase to phase U) |  | kV | 11 |  |
|  | - Rated voltage Um |  | kV | 12 |  |
|  | - Lighting impulse withstand voltage (peak) |  | kV | 75 |  |
|  | - Power frequency withstand voltage - 1 minutes |  | kV | 28 |  |
|  | - Requirement of Joint design |  |  |  |  |
|  | (i) Straight through joints |  | - | Heat shrink type |  |
|  | - Metallic radial water barrier |  | - | Yes/no |  |
|  | Manufacturer’s Quality Certification |  |  | ISO 9001 or equivalent |  |
|  | - Name of Certifying authority |  | - |  |  |
|  | - Year of Validity of the Certification |  | - |  |  |
|  | Requirement of Type test |  |  |  |  |
|  | - Name of Independent test authority |  | - |  |  |
|  | - Standard for type test |  | - | IEC60502-4 |  |
| 10.2 | 11 kV GIS cable termination |  |  |  |  |
|  | - Name of Manufacturer |  | - |  |  |
|  | - Location of manufacturing site |  | - |  |  |
|  | - Manufacturing and test standards |  | - | CENELEC EN50180, EN50181 & HD929 |  |
|  | - Type of termination |  | - | plug-in type |  |
|  | - Nominal operating voltage (phase to earth U0) |  | kV | 6.35 |  |
|  | - Nominal operating voltage (phase to phase U) |  | kV | 11 |  |
|  | - Rated voltage Um |  | kV | 12 |  |
|  | - Rated Continuous current |  | A |  |  |
|  | - Lightning impulse withstand voltage (peak) |  | kV | 75 |  |
|  | - Power frequency withstand voltage – 1 minutes |  | kV | 28 |  |
|  | Manufacturer’s Quality Certification |  |  | ISO 9001 or equivalent |  |
|  | - Name of Certifying authority |  | - |  |  |
|  | - Year of Validity of the Certification |  | - |  |  |
|  | Requirement of Type test |  |  |  |  |
|  | - Name of Independent test authority |  | - |  |  |
|  | - Standard for type test |  |  | CENELEC EN50180, EN50181 & HD929 |  |

TRANSFORMERS AND ASSOCIATED EQUIPMENT

| No. | Item | Units | Required | Tendered |
| --- | --- | --- | --- | --- |
| 30 MVA, 132/11 kV Transformer |  |  |  |  |
| (a) | Rating and Performance |  |  |  |
| 1. | Manufacturer's Name & Address |  |  |  |
| 2. | Continuous maximum rating (ONAN/ONAF) | MVA | 24/30 |  |
| 3. | Number of phases |  | 3 |  |
| 4. | Rated Frequency | Hz | 50 |  |
| 5. | Number of windings |  | 2 |  |
| 6. | Applicable standards |  | IEC 60076:2011 |  |
| 7. | System maximum voltage for both windings Um | HV | 145kV |  |
|  |  | MV | 12kV |  |
| 8. | Insulation type | HV | Graded |  |
|  |  | MV | Uniform |  |
| 9. | Highest Voltage for equipment | HV | 145kV |  |
|  |  | MV | 12kV |  |
| 10. | Winding insulation level. | HV | LI: 650kV, AC: 275 kV |  |
|  |  | MV | LI:75 kV, AC:28kV |  |
| 11. | Transformer Nominal Ratio |  | 132kV / 11 kV |  |
| 12. | Phase connections: |  |  |  |
|  | HV winding |  | Star |  |
|  | LV winding |  | Star |  |
|  | Vector Group |  | YNyn0 |  |
| 13. | Short circuit withstand fault level at terminals of |  |  |  |
|  | - 145 kV busbars | kA | 40 |  |
|  | - 12 kV busbars | kA | 25 |  |
|  | Short Circuit withstand current | sec | 3 |  |
| 14. | Type of Cooling |  | ONAN/ONAF |  |
| 15. | External cooling medium |  | Air |  |
| 16. | Service conditions: |  |  |  |
|  | Altitude not exceeding | m | 1000 |  |
|  | Air temperature not exceeding | °C | 45 |  |
|  | Average air temperature in any one year not exceeding |  |  |  |
|  | In any one day | °C | 32 |  |
|  | Average in one year | °C | 30 |  |
| 17. | On-load tap changer |  |  |  |
|  | (A) Type |  | M.R. (Germany) or Hitachi Energy (Sweden) |  |
|  | (B) Category of voltage control |  | CFVV |  |
|  | (C) HV or LV winding |  | HV |  |
|  | (D) Range (+ & -) | % | +10, -10 |  |
|  | (E) Step size | % | 1.25 |  |
|  | (F) Power frequency withstand test voltage between first and last contacts of the selector switch between any two adjacent contacts of the selector between diverter and switch contacts | (kV) |  |  |
|  | (G) Type test certificate reference |  |  |  |
|  | Tap position Indication | 2nos BCD |  |  |
| 18. | Size of tapping step with position nos. |  | 16 steps (+10 to -10) and 17 positions |  |
| 19. | Approximate ONAN rating | MVA | 24 |  |
| 20. | Winding temperature rise at CMR | °C | 65 – (Annual Average temperature - 20) |  |
| 21. | Top oil temperature rise |  |  |  |
|  | (A) CMR | °C | 60 – (Annual Average temperature - 20) |  |
|  | (B) ONAN rating | °C |  |  |
| 22. | Maximum hot spot temperature at CMR | °C | 98 |  |
| 23. | Maximum winding hot spot temperature of transformer at - Normal Cyclic Loading (IEC 60076-7) - Long time emergency loadings (IEC 60076-7) - Short time emergency loading (IEC 60076-7) | °C °C °C | 120 140 160 |  |
| 24. | Flux density in iron at normal voltage and frequency and at normal ratio - (no load). |  |  |  |
|  | (A) Core | Tesla |  |  |
|  | (B) Yokes | Tesla |  |  |
| 25. | Magnetizing current (approx.) at nominal ratio and |  |  |  |
|  | - at 0.9 x nominal voltage | % |  |  |
|  | - at 1.0 x nominal voltage | % |  |  |
|  | - at 1.1 x nominal voltage | % |  |  |
|  | - at 1.2 x nominal voltage | % |  |  |
| 26. | Guaranteed Losses at nominal ratio |  |  |  |
|  | (A) No Load losses (at rated voltage and frequency) (: To be applied for Loss evaluation) | kW | Max. 25 |  |
|  | (B) Copper losses at CMR corrected to 750C (: To be applied for Loss evaluation) | kW | Max. 150 |  |
|  | (C) Auxiliary losses at CMR corrected to 750C | kW |  |  |
| 27. | Regulation at 750C and normal ratio |  |  |  |
|  | (A) At unity power factor | % |  |  |
|  | (B) At 0.8 lagging power factor | % |  |  |
| 28. | Impedance voltage at 75 0C and CMR. Between |  |  |  |
|  | HV and LV Windings at Tap |  |  |  |
|  | Maximum | % |  |  |
|  | Nominal | % | 11 |  |
|  | Minimum | % |  |  |
| 29. | Equivalent circuit zero sequence impedance between HV and LV windings | ohms |  |  |
| 30. | Maximum current density in windings at C.M.R. |  |  |  |
|  | (A) HV Winding | A/mm2 |  |  |
|  | (B) LV Winding | A/mm2 |  |  |
| (b) | Control Circuits |  |  |  |
| 31. | Type of controls for on load tap changer and cooler controls |  | Automatic |  |
| 32 | Reference voltage (VT output line to line) | V | 110 AC (50Hz) |  |
| 33. | Whether load compensation required on the AVR |  | Yes |  |
| 34. | Whether separate remote-control panel required |  | Yes |  |
| 35. | Estimated distance between remote control point and transformer | m | <110 |  |
| 36. | DC supply (control voltage): |  |  |  |
|  | - Nominal | V | 110 V DC |  |
|  | - Maximum float voltage | V |  |  |
| 37. | AC supply voltage for tap changer operating motor 3 phase: |  | 400V AC 50 Hz |  |
| 38. | Whether marshalling kiosk required |  |  |  |
| 39. | Number of transformers for which automatic control is to be provided |  | All |  |
| 40. | Transformer terminals for line and neutral |  |  |  |
|  | (i) HV line |  | Cable Terminal Chamber |  |
|  | (ii) Neutral |  | Single- contact elbow bushings |  |
|  | (iii) LV line |  | multi-contact elbow bushing |  |
|  | (attach all technical data of all types of bushings & ducts) |  |  |  |
| 41. | Accommodation for current transformers in bushings at |  |  |  |
|  | (i) HV line |  |  |  |
|  | (ii) Neutral |  |  |  |
|  | (iii) LV line |  |  |  |
| 41.1 | HV neutral current transformers |  |  |  |
|  | (i) Name of Manufacturer |  |  |  |
|  | (ii) Country |  |  |  |
|  | (iii) No. of cores |  | See Scope of Works and Drawings |  |
|  | (iv) Protection cores |  |  |  |
|  | - Ratio | A | 400/1 |  |
|  | - Class |  | 5P20 |  |
|  | - Burden | VA |  |  |
|  | - Ratio | A | 400/1 |  |
|  | - Class |  | 5P20 |  |
|  | - Burden | VA |  |  |
| 41.2 | LV neutral current transformers |  |  |  |
|  | - Name of Manufacturer |  |  |  |
|  | - Country |  |  |  |
|  | - No. of cores |  | See Scope of Works and Drawings |  |
|  | - Protection cores |  |  |  |
|  | - Ratio | A | 2500/1 |  |
|  | - Class |  | 5P20 |  |
|  | - Burden | VA |  |  |
|  | - Ratio | A | 2500/1 |  |
|  | - Class |  | 5P20 |  |
|  | - Burden | VA |  |  |
| 43. | Pollution category of bushings. 53.7mm/kV based on system highest voltage for outdoor |  |  |  |
| (c) | Cooling |  |  |  |
| 1. | Minimum number of radiators per transformer |  |  |  |
| 2. | Maximum rating of each radiator as percentage of total loss at CMR |  |  |  |
| (d) | General |  |  |  |
| 1. | Type of oil preservation system |  | Silica Gel |  |
| 2. | Whether wheels, skid or flat bottom base required |  | Wheels |  |
| 3. | Transformer maximum noise acceptance level | dB | 62 |  |
| (e) | Details Of Construction |  |  |  |
| 1. | Types of winding - |  |  |  |
|  | (A) HV |  |  |  |
|  | (B) MV |  |  |  |
| 2. | Material of Insulation |  |  |  |
|  | (A) HV windings. |  |  |  |
|  | (B) LV windings |  |  |  |
| 3. | Insulation of tapping connections |  |  |  |
| 4. | Insulation of - |  |  |  |
|  | (A) Yoke bolts. |  |  |  |
|  | (B) Side plates. |  |  |  |
| 5. | Winding connections brazed or crimped Specify material (winding material and the joint material) |  |  |  |
| 6. | Is facility provided for adjustment of axial pressure on windings. | Yes/No |  |  |
| 7. | Thickness of transformer tank |  |  |  |
|  | (A) Sides | mm |  |  |
|  | (B) Bottom | mm |  |  |
| 8. | Material used for gaskets for oil tight joints. |  |  |  |
| 9. | Cover flange: - |  |  |  |
|  | Level: Low/High |  |  |  |
|  | Joint: WELDED/GASKETTED |  |  |  |
| (f) | Radiators Valves and Fans |  |  |  |
| 1. | Thickness of radiator plates and/or cooling tubes. | mm |  |  |
| 2. | Valve type/material: |  |  |  |
|  | - 75mm and below |  |  |  |
|  | - above 75mm |  |  |  |
| 3. | Equipment for ONAN cooling state (A) or (B) |  |  |  |
|  | (A) Radiator on main tank |  |  |  |
|  | (B) Separate cooler bank |  |  |  |
| 4. | Number of cooling air blowers per transformer |  |  |  |
| 5. | Speed of air blowers and air flow | rpm /m³ per min |  |  |
| 6. | Rating of each air blower motor | kW |  |  |
| 7. | Starting current of each blower motor, | A |  |  |
| (g) | Oil Volumes and Weights |  |  |  |
| 1. | Total oil required including cooler system | liters |  |  |
| 2. | Volume of oil to fill transformer to above the top yoke. | liters |  |  |
| 3. | Total volume of conservator | liters |  |  |
| 4. | Volume of oil in conservator between highest and lowest visible | liters |  |  |
| 5. | Weight of core and winding assembly | tons |  |  |
| 6. | Weight of each oil cooler bank complete with oil if mounted separately from transformer | tons |  |  |
| 7. | Total weights of complete transformers, including attached coolers, voltage regulating equipment, all fittings and oil | tons |  |  |
| 8. | Weight of transformer arranged for transport | tons |  |  |
| (h) | Transformer Oil |  |  |  |
| 1. | Manufacture, type and class of oil to IEC 60296 |  |  |  |
| (i) | Transformer tank Fittings |  |  |  |
| 1 | Draining and filter valves |  | yes |  |
| 2 | Valves for tank oil sampling |  | yes |  |
| 3 | Radiator isolation valves |  | yes |  |
| 4 | Pulling eyes for complete transformer |  | yes |  |
| 5 | Supports for hydraulic jacks |  | yes |  |
| 6 | Lifting lugs |  | yes |  |
| 7 | Tank earth terminals |  | yes |  |
| 8 | Core earth terminal box |  | yes |  |
| 9 | Inspection manholes |  | yes |  |
| 10 | Ladder |  | yes |  |
| 11 | Skids or wheels adjustable in two directions |  | yes |  |
| (j) | Transformer accessories |  |  |  |
| 1 | Oil preservation system with or without rubber bag |  | Yes |  |
| 2 | Dehydrating breather (maintenance free Type) |  | Yes |  |
| 3 | Oil level indicator of magnetic type |  | Yes |  |
| 4 | Contact thermometer for the oil temperature |  | Yes |  |
| 5 | Winding temperature indicator |  | Yes |  |
| 6 | Direct winding temperature measurement using fibre optic sensors |  | Yes |  |
| 7 | Pressure relief device |  | Yes |  |
| 8 | Rapid pressure relay |  | Yes |  |
| 9 | Buchholz relay |  | Yes |  |
| 10 | Buchholz relay gas sampling |  | Yes |  |
| 11 | Fire protection system |  | Yes |  |
| (k) | Quality Assurance |  |  |  |
| 1 | Manufacturer quality assurance acc. to ISO 9001 |  | Yes |  |
| 2 | Manufacturer Quality Manual is submitted with offer |  | Yes |  |
| 3 | Manufacturer a sample of Quality Inspection and Test Plan is submitted with offer |  | Yes |  |
| (l) | Routine tests at manufacturers works (IEC 60076-1:2011) |  |  |  |
| 1 | Measurement of winding resistance (11.2). |  | Yes |  |
| 2 | Measurement of voltage ratio and check of phase displacement (11.3). |  | Yes |  |
| 3 | Measurement of short-circuit impedance and load loss (11.4). |  | Yes |  |
| 4 | Measurement of no-load loss and current (11.5). |  | Yes |  |
| 5 | Dielectric routine tests (IEC60076- 3). |  | Yes |  |
| 6 | Tests on on-load tap-changers (11.7). |  | Yes |  |
| 7 | Leak testing with pressure for liquid- immersed transformers (tightness test) (11.8). |  | Yes |  |
| 8 | Check of the ratio and polarity of built-in current transformers. |  | Yes |  |
| 9 | Check of core and frame insulation for liquid immersed transformers with core or frame insulation (11.12). |  | Yes |  |
| 10 | Insulation of Auxiliary wiring (IEC 60076, part 3) |  | Yes |  |
| 11 | Partial discharge measurement (IEC 60076, part 3 |  | Yes |  |
| 12 | Determination of capacitances windings-to-earth and between windings |  | Yes |  |
| 13 | Measurement of d.c. insulation resistance between each winding to earth and between windings. |  | Yes |  |
| 14 | Measurement of dissipation factor (tan δ) of the insulation system capacitances. |  | Yes |  |
| 15 | Measurement of no-load loss and current at 90 % and 110 % of rated voltage (11.5). |  | Yes |  |
| (m) | Special tests |  |  |  |
| 1 | Dielectric special tests (IEC60076- 3). |  | Yes |  |
| 2 | Winding hot-spot temperature-rise measurements. |  | Yes |  |
| 3 | Determination of capacitances windings-to-earth, and between windings. |  | Yes |  |
| 4 | Measurement of dissipation factor (tan δ) of the insulation system capacitances. |  | Yes |  |
| 5 | Determination of transient voltage transfer characteristics (Annex B of IEC60076-3:2000). |  | Yes |  |
| 6 | Measurement of zero-sequence impedance(s) on three-phase transformers (11.6). |  | Yes |  |
| 7 | Short-circuit withstand test (IEC60076-5). |  | Yes |  |
| 8 | Measurement of d.c. insulation resistance each winding to earth and between windings. |  | Yes |  |
| 9 | Vacuum deflection test on liquid immersed transformers (11.9). |  | Yes |  |
| 10 | Pressure deflection test on liquid immersed transformers (11.10). |  | Yes |  |
| 11 | Vacuum tightness test on site on liquid immersed transformers (11.11). |  | Yes |  |
| 12 | Measurement of frequency response (Frequency Response Analysis or FRA). The test procedure shall be agreed between manufacturer and purchaser. |  | Yes |  |
| 13 | Check of external coating (ISO 2178 and ISO 2409 or as specified). |  | Yes |  |
| 14 | Measurement of dissolved gasses in dielectric liquid. |  | Yes |  |
| 15 | Mechanical test or assessment of tank for suitability for transport (to customer specification). |  | Yes |  |
| 16 | Determination of weight with transformer arranged for transport. For transformers up to 1,6 MVA by measurement. For larger transformers by measurement or calculation as agreed between manufacturer and purchaser. |  | Yes |  |
| 17 | Measurement of the harmonics of the on-load current |  | Yes |  |
| 18 | Insulation test of oil and Measurement of dielectric strength of oil |  | Yes |  |
| (n) | Site tests |  |  |  |
| 1 | insulation resistance measurement of core and frame insulation, winding insulation to earth and between windings |  | Yes |  |
| 2 | frequency response analysis |  | Yes |  |
| 3 | interrogation of shock recorders fitted for transport |  | Yes |  |
| 4 | Voltage ratio |  | Yes |  |
| 5 | Vector group |  | Yes |  |
| 6 | Insulation resistance measurement |  | Yes |  |
| 7 | Check of protective earthing connections |  | Yes |  |
| 8 | Current transformer polarity check |  | Yes |  |
| 9 | Control equipment circuit check |  | Yes |  |
| 10 | Oil tests |  | Yes |  |
| 11 | Operation test of supervisory equipment |  | Yes |  |
| 12 | Operation test of cooling equipment |  | Yes |  |
| 13 | Operation test of on load tap changer |  | Yes |  |
| 14 | Visual Inspections and adjustments as per clause 10.24 of technical specifications |  | Yes |  |
| 15 | fingerprint tests (Um>72 kV) |  | Yes |  |

| Auxiliary Transformers 200kVA 11/0.4kV |  |  |  |  |
| --- | --- | --- | --- | --- |
| (a) | General |  |  |  |
| 1. | Manufacturer's Name & Address |  |  |  |
| 2. | Location of installation |  |  |  |
| 4. | Single or three-phase unit |  | Three-phase unit |  |
| 5. | Core or shell type |  |  |  |
| 6. | Type of tank |  |  |  |
| 7. | Tank fully vacuum proof |  |  |  |
| 8. | Number of windings |  |  |  |
| 9. | Specification of oil |  |  |  |
| 10. | System voltages |  |  |  |
|  | - primary | kV | 11 |  |
|  | - secondary | kV | 0.4 |  |
| (b) | Ratings |  |  |  |
| 1. | Rated power | kVA | 200 |  |
| 2. | Rated symmetrical short circuit current | kA |  |  |
| 3. | Rated voltages (no load) |  |  |  |
|  | - primary | kV | 11 |  |
|  | - secondary | kV | 0.4 |  |
| 4. | Vector group symbol |  | Dny11 |  |
| 5. | Rated frequency | Hz | 50 |  |
| (c) | Service Conditions |  |  |  |
|  | - Maximum ambient temperature | °C |  |  |
|  | - Maximum service altitude | m | 1000 |  |
| 1. | Temperature rise limit - oil / windings | K | 60/65 |  |
| 2. | Impedance voltage at rated power between H.V. and L.V. windings | % | 4.5 |  |
| 3. | Zero sequence impedance per phase (L.V. winding unloaded) | Ohms |  |  |
| 4. | Magnetic flux density at rated voltage and frequency | Tesla |  |  |
| 5. | No-load losses (To be applied for loss evaluation) | kW |  |  |
| 6. | Load losses at full rated power of L.V. winding (To be applied for loss evaluation) | kW |  |  |
| 7. | No load Tap changer |  |  |  |
|  | 7.1. Manufacture & country |  |  |  |
|  | 7.2. Type & Form |  |  |  |
|  | 7.3. Location & Tap range |  | HV & +/- 5% |  |
|  | 7.4. step | % | 2.5% (5P) |  |
| (d) | Insulation level and Tests |  |  |  |
| 1. | Highest voltage for equipment |  |  |  |
|  | - primary winding | kV | 12 |  |
|  | - secondary winding | kV | 0.44 |  |
| 2. | Routine tests according to IEC 60076 series on each unit |  |  |  |
| 3. | Full-wave lightning impulse test |  |  |  |
|  | - Type test on each unit |  |  |  |
|  | - test Voltage / primary | kV | 75 |  |
| (e) | Operating Details |  |  |  |
| 1. | Cooling method |  | ONAN |  |
| 2. | Noise level at measuring distance of 0.3 m | dB(A) | 60 |  |
| (f) | Construction Details |  |  |  |
| 1. | Bottom base type |  |  |  |
| 2. | Terminations: |  |  |  |
|  | - HV |  | Cable Box |  |
|  | - LV |  | Cable Box |  |
|  | - Neutral |  | Cable box |  |
| (g) | Masses, Measures and Drawings |  |  |  |
| 1. | Overall dimensions including bushings |  |  |  |
|  | - height | mm |  |  |
|  | - depth | mm |  |  |
|  | - width | mm |  |  |
|  | Shipping dimensions |  |  |  |
|  | - height | mm |  |  |
|  | - depth | mm |  |  |
|  | - width | mm |  |  |
| 2. | Total mass of transformer completes as in service | kg |  |  |
| 3. | Transportation mass | kg |  |  |
| 4. | Un-tanking mass | kg |  |  |
| 5. | Mass of insulating liquid | kg |  |  |
| 6. | Minimum space requirements for transformer bay |  |  |  |
|  | - width | m |  |  |
|  | - depth | m |  |  |
| Diesel Generator |  |  |  |  |
| 1. | Manufacturer's Name & Address |  |  |  |
| 2. | Type |  |  |  |
| 3. | Rating | kVA | 20 |  |
| Water Fire Fighting System for Transformer |  |  |  |  |
| 1. | Manufacturer's Name & Address |  |  |  |
| 2. | Country |  |  |  |
| 3. | Standards to which conforms |  |  |  |
| Energy Meters |  |  |  |  |
| (a) | Meters |  |  |  |
| 1. | Manufacturers name & address |  |  |  |
| 2. | Manufactures Type designation and model number. |  |  |  |
| 3. | Dimensions |  |  |  |
|  | - width | mm |  |  |
|  | - height | mm |  |  |
|  | - depth | mm |  |  |
| 4. | Type |  | Digital Technology, Term "Interval Meters" - Accumulate pulse over a definite time interval. |  |
| 5. | Analog Inputs |  |  |  |
|  | Current AC | A | 1-5A |  |
|  | Voltage AC | V | 110/220V |  |
| 6. | Accuracy Class |  | 0.20% |  |
|  | Tolerance for all acceptance tests at unity power factor expressed in percent | % | 0.20% |  |
|  | Tolerance for all acceptance tests at 50% power factor expressed in percent | % | 0.30% |  |
| 7. | Pulse Resolution of the Energy transferred within |  | + or - 0.05% of the Energy measured |  |
| 8. | Measure Produce and Store Import Wh | Yes/No | Yes |  |
|  | Measure Produce and Store Export Wh | Yes/No | Yes |  |
|  | Measure Produce and Store Leading VArh. | Yes/No | Yes |  |
|  | Measure Produce and Store Lagging VArh. | Yes/No | Yes |  |
|  | Measure Produce and StroeV^2H per Phase | Yes/No | Yes |  |
|  | Measure Produce and Store I^2H per Phase | Yes/No | Yes |  |
|  | Date and Time | Yes/No | Yes |  |
| 9. | Capability of Storing 15 min time stamped interval data for 3 months period | Yes/No | Yes |  |
| 10. | Number of Events readable and maintain in the event logger | Nos | 100 |  |
| 11. | Remote interrogation over a Varity of communication media |  | Yes |  |
| 12. | Internal or external modem speed | bit/sec | 9600 |  |
| 13. | Availability of RS - 485 communication port | Yes/No | Yes |  |
|  | Availability of RS - 232 communication port | Yes/No | Yes |  |
|  | Support Public telecommunication system | Yes/No | Yes |  |
|  | Support Itron C&I Network | Yes/No | Yes |  |
|  | Support TCP/IP | Yes/No | Yes |  |
|  | Support ARDIS | Yes/No | Yes |  |
|  | Front Panel Optical port | Yes/No | Yes |  |
|  | Digital or Analog Cellular | Yes/No | Yes |  |
| 14. | Password protection in two levels for meter data collection | Yes/No | Yes |  |
|  | Read only access to interval data, event log, and metrological quantities | Yes/No | Yes |  |
|  | Full access to set the time function | Yes/No | Yes |  |
| 15. | Built in Battery backup capability to store and maintain interval data, event log & clock time | days | 35 |  |
| 16. | Clock time drift | minutes | <1 |  |
| 17. | Condition monitoring with recording in event log for failure in measuring and pulse over run | Yes/No | Yes |  |
| 18. | Possibility of uploading and detect faulty equipment conditions. | Yes/No | Yes |  |
| 19. | Sealability of Meters to prevent from: |  |  |  |
|  | - access to adjustment or calibration devices on meter. | Yes/No | Yes |  |
|  | - access to terminals of incoming current or potential wiring. | Yes/No | Yes |  |
| 20. | External Display showing the registers of total kWH and kVAR | Yes/No | Yes |  |

CIVIL WORKS

AIR CONDITIONING & VENTILATING INSTALLATIONS

| No. |  | Item | Units | Required | Tendered |
| --- | --- | --- | --- | --- | --- |
| Air Conditioning Units |  |  |  |  |  |
| (a) |  | Split type Air Conditioning Unit |  |  |  |
|  |  | Manufacturer’s name & address |  |  |  |
|  |  | Number of units |  |  |  |
|  |  | Country of origin |  |  |  |
|  |  | Type |  |  |  |
|  |  | Model No |  |  |  |
|  |  | Cooling duty (latent) | kW |  |  |
|  |  | Cooling duty (sensible) | kW |  |  |
|  |  | On – coil condition | DB/WB °C |  |  |
|  |  | Off – coil condition | DB/WB °C |  |  |
|  |  | Total electrical input | kW |  |  |
|  |  | Air volume | m3/hr |  |  |
|  |  | Total electrical input | kW |  |  |
|  |  | Electrical supply | N/m2 |  |  |
|  |  | Pre-filter manufacturer and type |  |  |  |
|  |  | Pre-filter size and pressure drop (clean) |  |  |  |
|  |  | Thermal insulation for refrigerant pipe work (if applicable) |  |  |  |
| (b) |  | Air Cooled Condensing Units |  |  |  |
|  |  | Number of Units |  |  |  |
|  |  | Manufacturer’s name and address |  |  |  |
|  |  | Country of origin |  |  |  |
|  |  | Type |  |  |  |
|  |  | Model No. |  |  |  |
|  |  | Refrigeration effect | kW each |  |  |
|  |  | Compressor type |  |  |  |
|  |  | Compressor input | kW each |  |  |
|  |  | Suction temperature | °C |  |  |
|  |  | Condenser ambient temperature | °C |  |  |
|  |  | Fan motor(s) | Total kW |  |  |
|  |  | Capacity steps | % |  |  |
| (c) |  | Self-contained Air Conditioning Units |  |  |  |
|  |  | Number of units |  |  |  |
|  |  | Manufacturer’s name and address |  |  |  |
|  |  | Country of origin |  |  |  |
|  |  | Type |  |  |  |
|  |  | Model No. |  |  |  |
|  |  | Refrigeration effect | kW each |  |  |
|  |  | Compressor input | kW each |  |  |
|  |  | Fan Motor | kW each |  |  |
| Ventilation Works |  |  |  |  |  |
|  | Manufacturer’s name and address |  |  |  |  |
|  | Number of units |  |  |  |  |
|  | Air volume |  | M3/hr |  |  |
|  | System resistance |  | N/m2 |  |  |
|  | Fan Motor size |  | KW |  |  |
|  | Corrosion protection |  |  |  |  |

FIRE SAFETY EQUIPMENT

| No. | Item | Units | Required | Tendered |
| --- | --- | --- | --- | --- |
| (a) | Trolley Mounted Extinguishers CO2 50kg |  |  |  |
|  | Manufacturer’s name and address |  |  |  |
|  | Dimensions | mm |  |  |
|  | Total weight | kg |  |  |
|  | Length of hose | mm |  |  |
|  | Type of powder |  |  |  |
|  | Working Pressure | kg/cm2 |  |  |
|  | Test Pressure | kg/cm2 |  |  |
|  | Numbers to be provided at |  |  |  |
| (b) | Wall Mounted Extinguishers CF 5.5 kg |  |  |  |
|  | Manufacturer’s name and address |  |  |  |
|  | Dimensions | mm |  |  |
|  | Total weight | kg |  |  |
|  | Length of hose | mm |  |  |
|  | Type of powder |  |  |  |
|  | Working Pressure | kg/cm2 |  |  |
|  | Test Pressure | kg/cm2 |  |  |
|  | Number to be provided at |  |  |  |
| (c) | Trolley Mounted Extinguishers BCF 50kg |  |  |  |
|  | Manufacturer’s name and address |  |  |  |
|  | Dimensions | mm |  |  |
|  | Total weight | kg |  |  |
|  | Length of hose | mm |  |  |
|  | Type of powder |  |  |  |
|  | Working Pressure | kg/cm2 |  |  |
|  | Test Pressure | kg/cm2 |  |  |
|  | Numbers to be provided at |  |  |  |

LIGHTING & SMALL POWER

| No. | Item | Units | Required | Tendered |
| --- | --- | --- | --- | --- |
| (a) | Distribution Boards (fitted with fuses) |  |  |  |
|  | Manufacturer’s name and address |  |  |  |
|  | Type and/or Figure No. |  |  |  |
|  | Rating | A |  |  |
|  | Fault rating | kA |  |  |
|  | Voltage | V |  |  |
| (b) | Distribution Boards (fitted with Circuit breakers) |  |  |  |
|  | Manufacturer’s name and address |  |  |  |
|  | Type and/or Figure No. |  |  |  |
|  | Rating | A |  |  |
|  | Fault rating | kA |  |  |
|  | Voltage | V |  |  |
| (c) | PVC Cable |  |  |  |
|  | Manufacturer’s name and address |  |  |  |
|  | Type |  |  |  |
|  | Voltage rating | V |  |  |
| (d) | Conduit |  |  |  |
|  | Manufacturer’s name and address |  |  |  |
|  | Type |  |  |  |
| (e) | Conduit Accessories |  |  |  |
|  | Manufacturer’s name and address |  |  |  |
|  | Type |  |  |  |
| (f) | Cable Termination’s |  |  |  |
|  | Manufacturer’s name and address |  |  |  |
|  | Type |  |  |  |
|  | Material |  |  |  |
| (g) | Switches |  |  |  |
|  | Manufacturer’s name and address |  |  |  |
|  | Type |  |  |  |
|  | Rating | W |  |  |
| (h) | Socket Outlets |  |  |  |
|  | Manufacturer’s name and address |  |  |  |
|  | Type and/or Figure No. |  |  |  |
|  | Rating | W |  |  |
|  | Finish |  |  |  |
| (i) | Contactors |  |  |  |
|  | Manufacturer’s name and address |  |  |  |
|  | Type |  |  |  |
|  | Rating | W |  |  |
|  | Number of contacts |  |  |  |
|  | Rating of coil AC | VA |  |  |
| (j) | Miniature Circuit Breakers |  |  |  |
|  | Manufacturer’s name and address |  |  |  |
|  | Type |  |  |  |
|  | Rating | A |  |  |
|  | Fault rating | kA |  |  |
| (k) | Earthing Material |  |  |  |
|  | Manufacturer’s name and address |  |  |  |
|  | Material & size |  |  |  |
| (l) | Clocks |  |  |  |
|  | Manufacturer’s name and address |  |  |  |
|  | Type |  |  |  |
|  | Size |  |  |  |
|  | Type of operation |  |  |  |
| (m) | Lighting fittings – Fluorescent |  |  |  |
|  | Manufacturer’s name and address |  |  |  |
|  | Type |  |  |  |
|  | Rating |  |  |  |
|  | Harmonic content |  |  |  |
| (n) | Lighting fittings - emergency |  |  |  |
|  | Manufacturer’s name and address |  |  |  |
|  | Type |  |  |  |
|  | Rating | W |  |  |
| (o) | Switch yard lighting |  |  |  |
|  | Manufacturer’s name and address |  |  |  |
|  | Type |  |  |  |
|  | Rating | W |  |  |

CCTV SYSTEM

| No. | Item | Units | Required | Tendered |
| --- | --- | --- | --- | --- |
|  | Manufacturer’s name and address |  |  |  |
|  | Country of origin |  |  |  |
|  | Type |  |  |  |
|  | Model No. |  |  |  |
|  | Image Sensor |  | ½” CCD |  |
|  | Horizontal resolution |  |  |  |
|  | Minimum illumination (when IR on) |  |  |  |
|  | S/N Ratio |  | More than 50db |  |
|  | Scanning System |  |  |  |
|  | Video output signal |  |  |  |
|  | IR Range |  |  |  |
|  | Number of Motion detection zones |  |  |  |
|  | Back Light Compensation |  |  |  |
|  | Auto Gain Control |  |  |  |
|  | IP Rating |  | IP 65 |  |
|  | Supply voltage |  |  |  |
| a) | Digital Video Recorder |  |  |  |
|  | Number of channels |  |  |  |
|  | Video compression |  |  |  |
|  | Hard disk capacity |  |  |  |
|  | Video monitor size |  |  |  |

LIGHTNING PROTECTION SYSTEM

| No. | Item | Units | Required | Tendered |
| --- | --- | --- | --- | --- |
|  | Manufacturer’s name and address |  |  |  |
|  | Country of origin |  |  |  |
|  | Type |  |  |  |
|  | Model No. |  |  |  |

INTRUDER PROTECTION SYSTEM

| No. | Item | Units | Required | Tendered |
| --- | --- | --- | --- | --- |
|  | Manufacturer’s name and address |  |  |  |
|  | Country of origin |  |  |  |
|  | Type |  |  |  |
|  | Model No. |  |  |  |

132KV GIS SUBSTATION

| No. | Item | Units | Required | Tendered |
| --- | --- | --- | --- | --- |
| 1. | 132kV GIS Building |  |  |  |
|  | Subcontractor’s name and address |  |  |  |
| 2. | Staff Quarters Buildings |  |  |  |
|  | Subcontractor’s name and address |  |  |  |