PART 2B

EMPLOYER’S REQUIREMENTS FOR
TRANSMISSION LINE WORK

APPENDIX - B1: TECHNICAL PARTICULARS

This page is intentionally left blank.

APPENDIX - B1: TECHNICAL PARTICULARS

Table of Contents

CLAUSE NO.	TITLE	PAGE NO.

1.	132 kV Triplex XLPE CABLE	1

2.	132kV CABLE ACCESSORIES	4

2.1	JOINTS	4

2.2	SF6 TYPE TERMINATIONS	4

2.3	OUTDOOR TYPE TERMINATION	4

3.	Distributed Temperature Sensing (DTS) system	5

4.	OPTICAL FIBER CABLES	5

5.	Tower	6

6.	Tower Grounding	7

7.	Conductors	7

8.	OPGW	8

9.	Insulators	10

10.	Foundation	11

This page is intentionally left blank.

The Bidder shall duly fill and complete the Technical Particulars. Non-completion and/or non-submission of the duly completed Technical Particulars may cause disqualification of the Bidder.

132 kV Triplex XLPE CABLE

| No. | Item Description | Unit | Required | Proposed |
| --- | --- | --- | --- | --- |
| 1. | Applicable standards |  | IEC 60840 |  |
| 2. | Type of Cable (Single core or Triplex type) |  | Triplex |  |
| 3. | Manufacturer/country |  |  |  |
| 4. | Year of first commercial operation of cable type offered |  |  |  |
| 5. | Nominal voltage (Uo/U) | kV | 76/132 |  |
| 6. | Frequency | Hz | 50 |  |
| 7. | Highest system voltage | kV | 145 |  |
| 8. | Number of cores |  | Three |  |
| 9. | Proposed cross-section | mm2 | 800 |  |
| 10. | Conductor: |  |  |  |
|  | - Material |  | Copper |  |
|  | - Shape |  | Milliken |  |
|  | - Diameter of conductor | mm |  |  |
|  | - Water stopper material in conductor |  | As per Specs |  |
|  | - Thickness of binder layer | mm |  |  |
|  | - Max. Continuous conductor temperature | °C | 90 |  |
|  | - Max. Short time conductor temperature | °C | 130 |  |
|  | - Applicable standard/clause |  | IEC60228 |  |
| 10. | Extruded conductor screen |  |  |  |
|  | - Material |  | As per Specs |  |
|  | - Nominal thickness | mm |  |  |
|  | - Minimum thickness | mm |  |  |
|  | - Diameter above conductor screen | mm |  |  |
| 11. | Insulation: |  |  |  |
|  | - Material |  | XLPE |  |
|  | - Nominal thickness | mm | 13.0 |  |
|  | - Minimum thickness at any point | mm |  |  |
|  | - Diameter above insulation | mm |  |  |
|  | - Details of vulcanization process |  | As per Specs |  |
|  | Extrusion method |  |  |  |
|  | Curing method |  | Dry |  |
|  | Cooling method |  |  |  |
| 12. | Insulation screen: |  |  |  |
|  | - Material |  | As per Specs |  |
|  | - Nominal thickness | mm |  |  |
|  | - Minimum thickness | mm |  |  |
|  | - Diameter above insulation screen | mm |  |  |
| 13. | Longitudinal sealing (Semi conductive swellable tape) |  |  |  |
|  | - Material |  | As per Specs |  |
|  | - Diameter above longitudinal sealing | mm |  |  |
| 14. | Metallic screen |  |  |  |
|  | - Material |  | Copper wire |  |
|  | - No. of strands | Nos. | 80 |  |
|  | - Nominal diameter of each wire | mm | 2.0 |  |
|  | - Minimum diameter of each wire | mm |  |  |
|  | - Maximum diameter of each wire | mm. |  |  |
|  | - Diameter above metallic screen | mm |  |  |
|  | - Longitudinal sealing details |  | As per Specs |  |
| 15. | Radial water protection layer |  | As per Specs |  |
|  | - Nominal thickness | mm |  |  |
|  | - Diameter above water protection layer | mm |  |  |
| 16. | Outer sheath |  |  |  |
|  | - Material |  | High density PE |  |
|  | - Colour |  | Black |  |
|  | - Nominal thickness | mm | 5.0 |  |
|  | - Minimum thickness at any point | mm |  |  |
|  | - Termite resistant | Yes/No | As per Specs |  |
|  | - Conductor coating | Yes/No | As per Specs |  |
| 17. | Overall diameter of completed cable | mm |  |  |
| 18 | Nominal weight of completed cable | kg/m |  |  |
| 19 | Allowable minimum radius of bend round which cable can be laid: |  |  |  |
|  | - Laid direct or in air | m |  |  |
|  | - In ducts | m |  |  |
|  | - For sealing ends | m |  |  |
| 20. | Maximum d.c. resistance of conductor at 20°C | μΩ/km | 0.0221 |  |
| 21. | Maximum a.c. resistance of conductor at 90°C | μΩ/km |  |  |
| 22. | Equivalent star reactance of three phase circuit at 50 Hz | μΩ/km |  |  |
| 23. | Maximum electrostatic capacitance per core | μF/km |  |  |
| 24. | Maximum charging current per conductor at nominal voltage | A/km |  |  |
| 25. | Maximum dielectric loss of three-phase circuit when operating at normal voltage and frequency at maximum conductor temperature of 90°C | W/km |  |  |
| 26. | Maximum continuous current carrying capacity per conductor when laid in the ground to a depth of 1200mm with ground temperature of 30°C and soil thermal resistivity 1.2°C m/W, conductor temperature of 90°C, load factor 1.0. |  |  |  |
|  | - One three-phase circuit per trench | A |  |  |
|  | - Two three-phase circuits at 400mm spacing | A |  |  |
| 27. | Maximum continuous current carrying capacity per conductor when drawn into ducts at a ground temperature of 300C and soil thermal resistivity 1.20Cm/W, conductor temperature of 90°C, load factor 1.0. |  |  |  |
|  | - One three-phase circuit in duct | A |  |  |
|  | - Two three-phase circuits at 680mm spacing | A |  |  |
| 28. | Maximum continuous current carrying capacity per conductor when installed in air at an ambient temperature of 450C and conductor temperature of 90°C |  |  |  |
|  | - One three-phase circuit | A |  |  |
|  | - Two three phase circuits at 1.0 m spacing | A |  |  |
| 29. | Metallic core screen losses in a cable of three-phase circuit at nominal voltage, 50 Hz frequency and at current ratings as given in item 27-a, b. | W/m |  |  |
| 30. | Total power losses (three phase system) | W/m |  |  |
| 31 | Conductor short-circuit permissible current when short-circuit occurs at conductor temperature of 90°C |  |  |  |
|  | Symmetrical three phase short circuit withstand current for: |  |  |  |
|  | - 0.1 sec | kA |  |  |
|  | - 0.2 sec | kA |  |  |
|  | - 0.5 sec | kA |  |  |
|  | - 1.0 sec | kA | 40 |  |
| 32. | Earth fault short-circuit current carrying capacity for 1 second, cable loaded as in Item 27(a) before short-circuit and final limiting temperature of outer sheath | kA | 40 |  |
| 33. | Maximum dielectric loss angle of charging VA of cable at normal voltage and frequency at a conductor temperature of:- |  |  |  |
|  | - 20 ºC |  |  |  |
|  | - 90 ºC |  |  |  |
| 34. | AC high voltage withstand voltage (30 min/ambient temperature) | kV | 190 |  |
| 35. | Impulse withstand voltage (90ºC) |  |  |  |
|  | - Positive 1/50 wave | kVp | 650 |  |
|  | - Negative 1/50 wave | kVp | 650 |  |
| 36. | Positive / Negative sequence impedance:- |  |  |  |
|  | - Resistance | μΩ/m |  |  |
|  | - Reactance | μΩ/m |  |  |
| 37. | Zero sequence impedance:- |  |  |  |
|  | - Resistance | μΩ/m |  |  |
|  | - Reactance | μΩ/m |  |  |
| 38. | Other Performance Data |  |  |  |
|  | - Maximum permissible pulling force of complete cable for nose pulling. | kN | 164 |  |
|  | - Maximum permissible sidewall pressure to cable at bending point | kN/m | 4.9 |  |
|  | - Nominal Delivery length per drum | m |  |  |
|  | - Gross weight of a delivery drum | kg |  |  |
|  | - Drum dimensions | mm |  |  |
|  | Shaft hole diameter | mm |  |  |
|  | Flange diameter | mm |  |  |
|  | Core diameter | mm |  |  |
|  | Width | mm |  |  |
|  | - Material of drum |  | Steel |  |
| 39. | Pipes/Ducts |  |  |  |
|  | - Nominal internal diameter of pipes/ducts | mm | 230 |  |
|  | - Material |  | HDPE |  |
|  | - Class/ Type |  |  |  |

132kV CABLE ACCESSORIES

| No. | Item Description | Unit | Required | Proposed |
| --- | --- | --- | --- | --- |
| JOINTS |  |  |  |  |
| 1. | Manufacturer/country |  |  |  |
| 2. | Type and designation |  |  |  |
| 3. | Rated system voltage | kV | 76/132 |  |
| 4. | Highest system voltage | kV | 145 |  |
| 5. | Impulse withstand voltage | kV | 650 |  |
| 6. | Rated frequency | Hz | 50 |  |
| 7. | Rated current | A | 700 |  |
| 8. | Rated short time withstand current (1sec) | kA | 40 |  |
| 9. | Conductor connecting method |  |  |  |
| 10. | Material of stress relief corn |  |  |  |
| 11. | Dimensions (Length, Diameter) | mm |  |  |
| 12. | Weight | kg |  |  |
| 13. | Provisions for cross bonding available | Yes/No |  |  |
| 14. | Provisions for Sheath integrity tests available | Yes/No |  |  |
| 15. | Applicable standards |  |  |  |
| SF6 TYPE TERMINATIONS |  |  |  |  |
| 1. | Manufacturer/Country |  |  |  |
| 2. | Type and designation |  |  |  |
| 3. | Rated system voltage | kV | 76/132 |  |
| 4. | Highest system voltage | kV | 145 |  |
| 5. | Impulse withstand voltage | kV | 650 |  |
| 6. | Rated frequency | Hz | 50 |  |
| 7. | Rated current | A | 700 |  |
| 8. | Rated short time withstand current (1sec) | kA | 40 |  |
| 9. | Insulator material |  |  |  |
| 10. | Dimensions (Height, Diameter) | mm |  |  |
| 11. | Weight | kg |  |  |
| 12. | Suitable for XLPE Cu Cable of Size | mm² |  |  |
| 13. | Provisions for periodic Sheath test available | Yes/No |  |  |
| 14. | Applicable Standards |  |  |  |
| OUTDOOR TYPE TERMINATION |  |  |  |  |
| 1. | Manufacturer/country |  |  |  |
| 2. | Type and designation |  |  |  |
| 3. | Rated system voltage | kV | 76/132 |  |
| 4. | Highest system voltage | kV | 145 |  |
| 5. | Impulse withstand voltage | kV | 650 |  |
| 6. | Rated frequency | Hz | 50 |  |
| 7. | Rated current | A | 700 |  |
| 8. | Rated short time withstand current (1sec) | kA | 40 |  |
| 9. | Insulator material |  |  |  |
| 10. | Creepage distance (minimum) | mm/kV | As per Specs |  |
| 11. | Pollution severity levels |  |  |  |
| 12. | Dimensions (height, diameter) | mm |  |  |
| 13 | Weight | kg |  |  |
| 14 | Suitable for XLPE Cu cable of size | mm2 |  |  |
| 15 | Applicable Standards |  |  |  |

Distributed Temperature Sensing (DTS) system

| No. | Item Description | Unit | Required | Proposed |
| --- | --- | --- | --- | --- |
| 1. | Applicable Standard |  |  |  |
| 2. | Manufacture/country |  |  |  |
| 3. | Fiber Mode (Single mode/Multimode) |  |  |  |
| 4. | Temperature accuracy | Degree C |  |  |
| 5. | - Spatial resolution | m |  |  |
| 6. | Measurable temperature range | Degree C |  |  |
| 7. | - Temperature resolution | Degree C |  |  |

OPTICAL FIBER CABLES

| No. | Item Description | Unit | Required | Proposed |
| --- | --- | --- | --- | --- |
| 1. | Applicable standards |  |  |  |
| 2. | Manufacturer/country |  |  |  |
| 3. | Type and designation |  |  |  |
| 4. | Number of fibers |  | 48 |  |
| 5. | Central strength member |  | FRP |  |
| 6. | Loose tube |  |  |  |
|  | - Material |  |  |  |
|  | - Diameter |  | Nom. 2.5mm |  |
| 7. | Filling compound in tube |  | Jelly |  |
| 8. | Inner sheath |  |  |  |
|  | - Material |  | HDPE |  |
|  | - Diameter |  |  |  |
| 9. | Strength element |  | Aramid yarn |  |
| 10. | Armoring |  |  |  |
|  | - Material |  |  |  |
|  | - Thickness |  |  |  |
| 11. | Outer sheath |  |  |  |
|  | - Material |  | HDPE |  |
|  | - Thickness |  |  |  |
|  | - Termite resistant | Yes/No |  |  |
| 12. | Cable diameter | mm |  |  |
| 13. | Weight of cable | kg/m |  |  |
| 14. | Mode field diameter at 1310nm |  | 9.0um+-0.5um |  |
| 15. | Mode field concentricity error |  | Max.0.8um |  |
| 16. | Cladding diameter |  | 125.0+-1.0um |  |
| 17. | Cladding non-circularity | % | Max1% |  |
| 18. | Attenuation |  |  |  |
|  | - at 1310nm | dB/km |  |  |
|  | - at 1550nm | dB/km |  |  |
| 19. | Dispersion at range 1285-1300nm | ps.nm.km |  |  |
| 20. | at 1550nm | ps/nm.km |  |  |
| 21. | Zero dispersion wavelength |  | <1310nm |  |
| 22. | Zero dispersion slope | ps/nm.km |  |  |
| 23. | Cable cut-off wavelength |  | <1270nm |  |

Tower

| No. | Item Description | Unit | Required | Proposed |
| --- | --- | --- | --- | --- |
| 1. | Applicable Standard |  |  |  |
| 2. | Manufacture/country |  |  |  |
|  | - Steel |  |  |  |
|  | - Bolts, nuts and washers |  |  |  |
|  | - Tower accessories |  |  |  |
| 3. | Line voltage | kV | 132 |  |
| 4. | Number of circuits | No. | 1 |  |
| 5. | Tower Type | - | Dead-end |  |
| 6. | Angle of deviation | Deg. | 30-60 |  |
| 7. | Designed span |  |  |  |
|  | - Standard span | m | 350 |  |
|  | - Wind span | m | 350 |  |
|  | - Weight span | m | 350 |  |
| 8. | Designed wind load |  |  |  |
|  | - Conductor | kg/m2 | 60.9 |  |
|  | - Steel angle members | kg/m2 | 98.5 |  |
|  | - Steel angle front and back of structure | kg/m2 | 168.5 |  |
| 9. | Safety factors for tower/foundation/conductor/OPGW | - | As per specs |  |
| 10. | Tower members and bolts |  |  |  |
| 10.1 | Structural members |  |  |  |
|  | - Tension based on net sectional area | kg/cm2 | 2600 |  |
|  | - Axial compression based on gross sectional area | kg/cm2 | 2550 |  |
| 10.2 | Connection bolts |  |  |  |
|  | - Shear on gross area | kg/cm2 | 2220 |  |
|  | - Bearing (on mild steel) | kg/cm2 | 4440 |  |
|  | - Tension on net area of threaded portion | kg/cm2 | 1980 |  |
| 10.3 | Slenderness Ratios (L/R) |  |  |  |
|  | - Main members | - | Bellow 150 |  |
|  | - Braces | - | Bellow 200 |  |
|  | - Redundant members | - | Bellow 250 |  |
|  | - Members loaded in tension only | - | Bellow 375 |  |
| 10.4 | Member particulars |  |  |  |
|  | - Calculated members | mm | 45x45x4 |  |
|  | - Redundant members | mm | 45x45x4 |  |
|  | - Thickness of legs, members in cross arms and in earth wire peaks | mm | 6 |  |
|  | - Diameter of bolts for member carrying stress | mm | 16 |  |
|  | - Diameter of bolts for redundant members without calculated stress | mm | 16 |  |
|  | - Gusset plates | mm | 6 |  |
|  | - Stub angles | mm | 8 |  |
| 10.5 | Dips and Tensions |  |  |  |
|  | - Nil wind at everyday temperature | m kN |  |  |
|  | - Full design wind pressure on conductor/OPGW at everyday temperature | m kN |  |  |
|  | - 36% full design wind pressure on conductor/OPGW at everyday minimum temperature. | m kN |  |  |
|  | - 75% full design wind pressure on conductor/OPGW at everyday temperature under broken wire condition | m kN |  |  |
|  | - Nil Wind at Minimum Temperature | m kN |  |  |
| 10.6 | Clearances |  |  |  |
|  | - Minimum ground clearance under maximum temperature and nil wind | m | 7.5 |  |
|  | - Min. clearance between conductor and tower | mm | 1500 |  |
|  | - Min. clearance between phases | mm | 3000 |  |
|  | - Height of lowest cross-arm above ground level | m | 16.0 |  |
| 10.7 | Shielding angle of OPGW | Deg. | 30 |  |
| 11. | Weight of special branch tower | kg |  |  |

Tower Grounding

| No. | Item Description | Unit | Required | Proposed |
| --- | --- | --- | --- | --- |
| 1. | Applicable Standard |  |  |  |
| 2. | Manufacture/country |  |  |  |
| 3. | Materials |  |  |  |
| 3.1 | Grounding rods |  |  |  |
|  | - Galvanized steel angle | mm | 50x50x5x2000 |  |
| 3.2 | Ground wire |  |  |  |
|  | - Galvanized steel wire | mm2 | 38 |  |
|  | - Galvanized steel strip | No./dia. mm | 7/2.6 |  |
| 4. | Required resistance value of tower | Ohm | Below 10 |  |

Conductors

| No. | Item Description | Unit | Required | Proposed |
| --- | --- | --- | --- | --- |
| 1. | Conductor |  |  |  |
| 1.1 | Applicable Standard |  |  |  |
| 1.2 | Manufacture/country |  |  |  |
| 1.3 | Conductor Code | - | DUCK |  |
| 1.4 | Particulars |  |  |  |
|  | - Conductor size | mm2 | 308.9 |  |
|  | - Number and size of wires |  |  |  |
|  | - Aluminum - Steel | No./dia. mm No./dia. mm | 54/2,69 7/2.69 |  |
|  | - Cross section |  |  |  |
|  | - Aluminum - Steel - Total | mm2 mm2 mm2 | 264.4 61.7 326.1 |  |
|  | - Conductor diameter | mm | 24.21 |  |
|  | - Ultimate strength | kg | 10,250 |  |
|  | - Modulus of elasticity final | N/mm2 | 8,200 |  |
|  | - Coefficient of linear expansion | 1/°C | 17.6 x 10-6 |  |
|  | - Standard mass of conductor | kg/km | 1,161 |  |
|  | - DC resistance at 25 °C | ohm/km | 0.09424 |  |
| 2. | Vibration dumper |  |  |  |
| 2.1 | Applicable Standard |  |  |  |
| 2.2 | Manufacture/country |  |  |  |
| 2.3 | Type |  | Stockbridge |  |
| 2.3 | Particulars |  |  |  |
|  | - Suitable for conductor size |  | For DUCK |  |
|  | - Total weight of each damper | kg |  |  |
|  | - The number of dumpers required per span | Nos. |  |  |
|  | - Position of fixing damper on the conductor from the clamp - mouth |  |  |  |
|  | - First damper | m |  |  |
|  | - Second damper | m |  |  |
|  | - Third damper | m |  |  |
|  | - Clamping torque | kg-m |  |  |
| 3. | Tension clamp |  |  |  |
| 3.1 | Applicable Standard |  |  |  |
| 3.2 | Manufacture/country |  |  |  |
| 3.3 | Particulars |  |  |  |
|  | - Suitable for conductor size |  | For DUCK |  |
|  | - Slip strength | kN |  |  |
|  | - Minimum failing load (No deformation) | kN |  |  |
|  | - Shape of cross section |  |  |  |
|  | - Before compression | mm2 |  |  |
|  | - After compression | mm2 |  |  |
|  | - Dimensions of sleeve |  |  |  |
|  | - Before compression | mm |  |  |
|  | - After compression | mm |  |  |
|  | - Length of sleeve |  |  |  |
|  | - Before compression | mm |  |  |
|  | - After compression | mm |  |  |
|  | - Electrical resistance of tension clamp as % of equivalent length of conductor | % |  |  |

OPGW

| No. | Item Description | Unit | Required | Proposed |
| --- | --- | --- | --- | --- |
| 1. | OPGW |  |  |  |
| 1.1 | Applicable standards |  |  |  |
|  | - Aluminum alloy wires | - | IEC 104 type A |  |
|  | - Aluminum clad steel wire | - | IEC 1232 |  |
|  | - Cable construction | - | IEC 1089 |  |
| 1.2 | Particulars |  |  |  |
|  | - No. of Fibers | No. | 48 |  |
|  | - Cross Section Area | mm2 | 87.13 |  |
|  | - Overall Diameter | mm | 12.8 |  |
|  | - Min Breaking Load | kN | 84.7 |  |
|  | - Unit Mass | kg/km | 560 |  |
|  | - DC Resistance at 200C | ohm/km | 0.743 |  |
|  | - Short Circuit Current for 0.5 sec | kA (0C) | 10 (200) |  |
|  | - Modulus Elasticity | MPa | 140 |  |
|  | - Coefficient of Linear Expansion | 1/°C | 13.4X10-6 |  |
|  | - Aluminum-clad steel wire Steel - Tube | No./dia. mm No./dia. mm | 6/4.3 1/1.4 |  |
| 2. | Optical fibers |  |  |  |
| 2.1 | Applicable standards | - | ITU-T G.652 |  |
| 2.2 | Particulars |  |  |  |
|  | - Type of optical fiber | - | Dual window, single-Mode |  |
|  | - Dimensions and geometry of fiber | - | According to ITU-T G.652 |  |
|  | - Attenuation Coefficient at 1310 nm at 200C | dB/km | ≤0.4 |  |
|  | - Attenuation Coefficient at 1550 nm at 200C | dB/km | ≤0.25 |  |
|  | - Attenuation deviation at 1310nm and 1550nm | dB/km | ≤0.1 within -450C to 800C |  |
|  | - Other properties of fiber | - | According to ITU-T G.652 |  |
| 3. | Tension assembly |  |  |  |
| 3.1 | Applicable standards |  |  |  |
| 3.2 | Manufacture/country |  |  |  |
| 3.3 | Particulars |  |  |  |
|  | - Structure; consists of - Hyper formed alum weld dead end grip - Associated hardware for earth wire attachment (shackle, link, clevis, clamps) - Flexible grounding loop connection |  |  |  |
|  | - Minimum slip strength | kN |  |  |
|  | - Minimum ultimate breaking strength | kN |  |  |
|  | - Total weight of complete assembly | kg |  |  |
|  | - Breaking strength of tension clamp as % of breaking load of OPGW | % |  |  |
|  | - Resistivity as % of equivalent length of OPGW | % |  |  |
| 4. | Vibration dumper |  |  |  |
| 4.1 | Applicable Standard |  |  |  |
| 4.2 | Manufacture/country |  |  |  |
| 4.3 | Type |  | Stockbridge |  |
| 4.4 | Particulars |  |  |  |
|  | - Suitable for OPGW size |  | For “1. OPGW” |  |
|  | - Total weight of each damper | kg |  |  |
|  | - The number of dumpers required per span | Nos. |  |  |
|  | - Position of fixing damper on the OPGW from the clamp mouth |  |  |  |
|  | - First damper | m |  |  |
|  | - Second damper | m |  |  |
|  | - Third damper | m |  |  |
|  | - Clamping torque | kg-m |  |  |
| 5. | Fiber Optic Splicing Box |  |  |  |
| 5.1 | Applicable Standard |  | IP 65 of IEC 60529 |  |
| 5.2 | Manufacture/country |  |  |  |
| 5.3 | Particulars |  |  |  |
|  | - Splice capacity for minimum number of fibers | Nos. | 96 |  |
|  | - Installation height on tower | m | 1.5 |  |

Insulators

| No. | Item Description | Unit | Required | Proposed |
| --- | --- | --- | --- | --- |
| 1. | Insulator unit |  |  |  |
| 1.1 | Applicable Standard |  | IEC 60383 IEC 61109 |  |
| 1.2 | Manufacture/country |  |  |  |
| 1.3 | Particulars |  |  |  |
|  | - Type of insulator |  | Toughened glass or porcelain disc |  |
|  | - Type of coupling | - | Ball & socket |  |
|  | - IEC designation | - | U120B |  |
|  | - Dimensions |  |  |  |
|  | - Spacing of insulator | mm appr. | 146 |  |
|  | - Diameter of sheds | mm appr. | 255 |  |
|  | - Creepage distance | mm appr. | 320 |  |
|  | - Minimum breaking load | kN | 120 |  |
|  | - Power frequency one minute withstand voltage |  |  |  |
|  | - Dry | kV(rms) | 70 |  |
|  | - Wet | kV(rms) | 40 |  |
|  | - Impulse withstand voltage | kV(peak) | 110 |  |
|  | - Power frequency puncture voltage | kV(rms) | 100 |  |
| 2. | Insulator string set |  |  |  |
| 2.1 | Applicable standards | - | IEC60437 |  |
| 2.2 | Manufacture/country |  |  |  |
| 2.3 | Particulars |  |  |  |
|  | - Number of units |  |  |  |
|  | - Single tension string | Nos. | Min. 10 |  |
|  | - Down dropper | Nos. | Min. 10 |  |
|  | - Ratio of horn gap length for tension string sets | - | More than 85% |  |
|  | - Power frequency one minute withstand voltage for tension string sets |  |  |  |
|  | - Dry | kV (rms) |  |  |
|  | - Wet | kV (rms) |  |  |
|  | - Power frequency flashover voltage for tension string sets | kV (rms) |  |  |
|  | - Impulse withstand voltage for tension string sets | kV(peak) |  |  |
|  | - Impulse flashover voltage for tension string sets | kV(peak) |  |  |
|  | - Corona extinction voltage for tension string sets | kV (rms) |  |  |
|  | - Maximum RIV for complete tension string set including arcing horns, clamps, etc. at 145 KV (rms) | dB(peak) |  |  |
|  | - Weight |  |  |  |
|  | - Single tension string | kg |  |  |
|  | - Down dropper | kg |  |  |

Foundation

| No. | Item Description | Unit | Required | Proposed |
| --- | --- | --- | --- | --- |
| 1. | Foundation |  |  |  |
| 1.1 | Foundation Type I: Spread footing with undercut |  |  |  |
|  | - Ultimate bearing capacity of soil | kg/mm2 | 1.5 |  |
|  | - Assumed cone of earth | degree | 30 |  |
|  | - Cohesive materials | - | Very stiff clay requiring picking for removal. A fresh sample of which can not be molded by finger pressure and intended by thumb. Blow count over 10. |  |
|  | - Granular material | - | Very dense cemented gravel. Difficult to excavate by shovel alone. Relative density over 75%. Blow count over 20. |  |
|  | - Length of stab | m |  |  |
|  | - Base size (square) and depth | m |  |  |
|  | - Volume of concrete per tower | m3 |  |  |
|  | - Mass of reinforcing steel per tower | kg |  |  |
| 1.2 | Foundation Type II: Spread Footing |  |  |  |
|  | - Ultimate bearing capacity of soil | kg/mm2 | 1.0 |  |
|  | - Assumed cone of earth | degree | 20 |  |
|  | - Cohesive materials |  | Stiff clay. Some silt and sand. Not readily excavated by shovel alone. Can not be molded by finger pressure and intended by thumb. Blow count 8 to 10. |  |
|  | - Granular material |  | Compacted sand. Some silt and gravel. Difficult to excavate by shovel alone. Relative density over 60%. Blow count 10 to 20. |  |
|  | - Length of stab |  |  |  |
|  | - Base size (square) and depth | m |  |  |
|  | - Volume of concrete per tower | m3 |  |  |
|  | - Mass of reinforcing steel per tower | kg |  |  |
| 1.3 | Foundation Type III: Spread Footing |  |  |  |
|  | - Ultimate bearing capacity of soil | kg/mm2 | 0.5 |  |
|  | - Assumed cone of earth | degree | 10 |  |
|  | - Cohesive materials |  | Soft to medium clay. Some silt and sand. Can be excavated by shovel alone and molded by medium finger pressure. Blow count 4 to 8. |  |
|  | - Granular material |  | Loose to medium sand and silt. Easily excavated by shovel alone and molded by medium finger pressure. Blow count 4 to 10. |  |
|  | - Length of stab | m |  |  |
|  | - Base size (square) and depth | m |  |  |
|  | - Volume of concrete per tower | m3 |  |  |
|  | - Mass of reinforcing steel per tower | kg |  |  |