PART 2C

EMPLOYER’S REQUIREMENTS FOR

DISTRIBUTION LINE WORK

APPENDIX - C1: TECHNICAL PARTICULARS

This page is intentionally left blank.

APPENDIX-C1: GUARANTEED TECHNICAL PARTICULARS

Table of Contents

CLAUSE NO.	TITLE	PAGE NO.

1.	11 kV XLPE Power Cable, 3 Core, 400 sq. mm Al. Conductor, XLPE & accessories	1

2.	11 kV XLPE Power Cable, 3 Core, 300 sq. mm Al. Conductor, XLPE & accessories	4

3.	11 kV XLPE Power Cable, 3 Core, 150 sq. mm Al. Conductor, XLPE & accessories	7

4.	11 KV XLPE INSULATED ALL ALUMINIUM ALLOY CONDUCTOR (AAAC)	10

5.	MULTIPLE CORE LT XLPE ARMOURED CABLES.	13

6.	LT XLPE ARMOURED SERVCIE CABLES	16

7.	11kV Outdoor Terminal Kit	19

8.	HDPE PN6 PIPE (For HDD method)	20

9.	HDPE PN4 PIPE (For open trench)	21

10.	11kV SF6 Extensible RMU	22

11.	LT Feeder Panel with MuLti-FunctionAL Meter	31

12.	11m Steel Tubular Pole	33

13.	9m Steel Tubular Pole	35

14.	Gang Operated SWitch	37

15.	Lightning Arrestor	39

16.	Pole Clamps	40

17.	Earth Rods and Clamps	41

18.	Grounding Conductor	42

19.	Galvanized Steel Nuts and Bolts	43

20.	High Voltage Warning/Danger Plate	44

21.	RTU (Remote Terminal Unit)	45

22.	FRTU (Feeder Remote Terminal Unit)	55

23.	SDH/MPLS Switchable Optical Terminal	63

24.	Underground Fiber Optic Cable (UGFO) – 24 Fibers	68

25.	Underground Fiber Optic Cable (UGFO) – 96 Fibers	69

26.	DUAL-WINDOW SINGLE MODE (DW-SM)	70

11 kV XLPE Power Cable, 3 Core, 400 sq. mm Al. Conductor, XLPE & accessories

| No. | DESCRIPTION | UNIT | NEA REQ. | DATA to be Filled |
| --- | --- | --- | --- | --- |
|  |  |  | 11 kV | 11 kV |
| 1 | Manufacturer and Country of Origin |  |  |  |
| 2 | Year of manufacturing experience | Years | 10 |  |
| 3 | Catalogue/drawing submitted |  | Yes |  |
| 4 | Applicable standard |  | IEC |  |
| 5 | Type |  |  |  |
| 7 | Number of Cores | No. | 3 |  |
| 8 | Rated Voltage | kV | 6/10 |  |
| 9 | Maximum System voltage | kV | 12 |  |
| 10 | Max. Rated Voltage between conductor and screen | kV | 6.9 |  |
| 11 | Rated Voltage between two conductors | kV | 11 |  |
| 12 | Conductor Material |  | Aluminum |  |
| 13 | Cross section of the Conductor | mm2 | 400 |  |
| 14 | Cross section of each wire | mm2 |  |  |
| 15 | No.& diameter of wire in each conductor | No./mm |  |  |
| 16 | Class of Stranding |  | Class 2 |  |
| 17 | Operating Capacitance | µF/km |  |  |
| 18 | Maximum Conductor Temperature | °C | 90 |  |
| 19 | Conductor screen material |  |  |  |
| 20 | Thickness of Conductor Screen | mm | 0.6 |  |
| 21 | Thickness of XLPE insulation | mm | 3.4 |  |
| 22 | Insulation screen material |  |  |  |
| 23 | Thickness of Insulation Screen | mm | 0.7 |  |
| 24 | Water Swelleable tape | Yes/No | Yes |  |
| 25 | Copper tape along with copper wire | Yes/No | Yes |  |
| 26 | Thickness of Copper Screen | mm | 0.1 |  |
| 27 | Nominal Thickness of PVC Inner sheath | mm |  |  |
| 28 | Copper Screen with water tight design | Yes/No | Yes |  |
| 29 | Armour Material and thickness |  |  |  |
| 30 | Nominal Thickness of HDPE Outer Sheath | mm |  |  |
| 31 | Overall Diameter of the Cable | mm |  |  |
| 32 | Continuous current rating at 45 deg. C. ambient |  |  |  |
|  | - in ground | A |  |  |
|  | - in duct | A |  |  |
| 33 | Short circuit current |  |  |  |
|  | - 0.1 sec | kA |  |  |
|  | - 1.0 sec (minimum kA) | kA |  |  |
| 34 | Electrical parameter |  |  |  |
|  | - Resistance/km |  |  |  |
|  | - Reactance/km |  |  |  |
|  | - Capacitance/km |  |  |  |
| 35 | Max. Partial Discharge |  |  |  |
| 36 | AC Test Voltage for 5 min. | kV |  |  |
| 37 | Insulation Level: |  |  |  |
|  | -Power frequency Withstand Voltage | kV |  |  |
|  | -Impulse Withstand, Crest | kV |  |  |
| 38 | Min. Insulation Resistance | ohms |  |  |
| 39 | Max. Conductor DC Resistance at 20 Deg. C | Ohm/km |  |  |
| 40 | Geometric Mean Radius (GMR) of the Cable/Conductor | mm |  |  |
| 41 | Fire resistance treated | Yes/No |  |  |
| 42 | Is manufacturer an ISO 9001 holder? | Yes/No | Yes |  |
| 43 | ISO 9001 (with design) certificate submitted? | Yes/No | Yes |  |
| 44 | Type test certificate submitted? | Yes/No | Yes |  |
| 45 | User's certificate submitted? | Yes/No | Yes |  |
| 46 | Standard drum length | Meter |  |  |
| 47 | Approx. Net Weight per Meter of cable | Kg |  |  |
| 48 | Net weight of cable in drum | Kg |  |  |
|  | Straight Through Joint |  |  |  |
| 49 | Manufacturer and Country of Origin |  |  |  |
| 50 | Year of manufacturing experience | Years | 10 |  |
| 51 | Catalogue Number |  |  |  |
| 52 | Copies of Governing Standards Attached |  | Yes |  |
| 53 | Applicable standard |  | IEC |  |
| 54 | Copies of type test attached | Yes/No | Yes |  |
| 55 | Type |  |  |  |
| 56 | Is Splice Kit Performed or Tape |  |  |  |
| 57 | Splicing voltage level | kV | 12 |  |
| 58 | Power frequency withstand voltage | kV | 21 |  |
| 59 | Impulse withstand voltage (BIL) | KV | 75 |  |
| 60 | Is ISO 9001 certificate submitted? | Yes/No | Yes |  |
| 61 | Technical literature/drawings submitted? | Yes/No | Yes |  |
| 62 | Embossing |  |  |  |

11 kV XLPE Power Cable, 3 Core, 300 sq. mm Al. Conductor, XLPE & accessories

|  | DESCRIPTION | UNIT | NEA REQ. | DATA to be Filled |
| --- | --- | --- | --- | --- |
| 1 | Manufacturer and Country of Origin |  |  |  |
| 2 | Year of manufacturing experience | Years | 10 |  |
| 3 | Catalogue/drawing submitted |  | Yes |  |
| 4 | Applicable standard |  | IEC |  |
| 6 | Type |  |  |  |
| 7 | Number of Cores | No. | 3 |  |
| 8 | Rated Voltage | kV | 6/10 |  |
| 9 | Maximum System voltage | kV | 12 |  |
| 10 | Max. Rated Voltage between conductor and screen | kV | 6.9 |  |
| 11 | Rated Voltage between two conductors | kV | 11 |  |
| 12 | Conductor Material |  | Aluminum |  |
| 13 | Cross section of the Conductor | mm2 | 300 |  |
| 14 | Cross section of each wire | mm2 |  |  |
| 15 | No.& diameter of wire in each conductor | No./mm |  |  |
| 16 | Class of Stranding |  | Class 2 |  |
| 17 | Operating Capacitance | µF/km |  |  |
| 18 | Maximum Conductor Temperature | °C | 90 |  |
| 19 | Conductor screen material |  |  |  |
| 20 | Thickness of Conductor Screen | mm | 0.6 |  |
| 21 | Thickness of XLPE insulation | mm | 3.4 |  |
| 22 | Insulation screen material |  |  |  |
| 23 | Thickness of Insulation Screen | mm | 0.7 |  |
| 24 | Water Swellable tape | Yes/No | Yes |  |
| 25 | Copper tape along with copper wire | Yes/No | Yes |  |
| 26 | Thickness of Copper Screen | mm | 0.1 |  |
| 27 | Nominal Thickness of PVC Inner sheath | mm |  |  |
| 28 | Copper Screen with water tight design | Yes/No | Yes |  |
| 29 | Armour Material and thickness |  |  |  |
| 30 | Nominal Thickness of HDPE Outer Sheath | mm |  |  |
| 31 | Overall Diameter of the Cable | mm |  |  |
| 32 | Continuous current rating at 45 deg. C. ambient |  |  |  |
|  | - in ground | A |  |  |
|  | - in duct | A |  |  |
| 33 | Short circuit current |  |  |  |
|  | - 0.1 sec | kA |  |  |
|  | - 1.0 sec (minimum kA) | kA |  |  |
| 34 | Electrical parameter |  |  |  |
|  | - Resistance/km |  |  |  |
|  | - Reactance/km |  |  |  |
|  | - Capacitance/km |  |  |  |
| 35 | Max. Partial Discharge |  |  |  |
| 36 | AC Test Voltage for 5 min. | kV |  |  |
| 37 | Insulation Level: |  |  |  |
|  | -Power frequency Withstand Voltage | kV |  |  |
|  | -Impulse Withstand, Crest | kV |  |  |
| 38 | Min. Insulation Resistance | ohms |  |  |
| 39 | Max. Conductor DC Resistance at 20 Deg. C | Ohm/km |  |  |
| 40 | Geometric Mean Radius (GMR) of the Cable/Conductor | mm |  |  |
| 41 | Fire resistance treated | Yes/No |  |  |
| 42 | Is manufacturer an ISO 9001 holder? | Yes/No | Yes |  |
| 43 | ISO 9001 (with design) certificate submitted? | Yes/No | Yes |  |
| 44 | Type test certificate submitted? | Yes/No | Yes |  |
| 45 | User's certificate submitted? | Yes/No | Yes |  |
| 46 | Standard drum length | Meter |  |  |
| 47 | Approx. Net Weight per Meter of cable | Kg |  |  |
| 48 | Net weight of cable in drum | Kg |  |  |
|  | Straight Through Joint |  |  |  |
| 49 | Manufacturer and Country of Origin |  |  |  |
| 50 | Year of manufacturing experience | Years | 10 |  |
| 51 | Catalogue Number |  |  |  |
| 52 | Copies of Governing Standards Attached |  | Yes |  |
| 53 | Applicable standard |  | IEC |  |
| 54 | Copies of type test attached | Yes/No | Yes |  |
| 55 | Type |  |  |  |
| 56 | Is Splice Kit Performed or Tape |  |  |  |
| 57 | Splicing voltage level | kV | 12 |  |
| 58 | Power frequency withstand voltage | kV | 21 |  |
| 59 | Impulse withstand voltage (BIL) | KV | 75 |  |
| 60 | Is ISO 9001 certificate submitted? | Yes/No | Yes |  |
| 61 | Technical literature/drawings submitted? | Yes/No | Yes |  |
| 62 | Embossing |  |  |  |

11 kV XLPE Power Cable, 3 Core, 150 sq. mm Al. Conductor, XLPE & accessories

| No. | DESCRIPTION | UNIT | NEA REQ. | DATA to be Filled |
| --- | --- | --- | --- | --- |
| 1 | Manufacturer and Country of Origin |  |  |  |
| 2 | Year of manufacturing experience | Years | 10 |  |
| 3 | Catalogue/drawing submitted |  | Yes |  |
| 4 | Applicable standard |  | IEC |  |
| 6 | Type |  |  |  |
| 7 | Number of Cores | No. | 3 |  |
| 8 | Rated Voltage | kV | 6/10 |  |
| 9 | Maximum System voltage | kV | 12 |  |
| 10 | Max. Rated Voltage between conductor and screen | kV | 6.9 |  |
| 11 | Rated Voltage between two conductors | kV | 11 |  |
| 12 | Conductor Material |  | Aluminum |  |
| 13 | Cross section of the Conductor | mm2 | 150 |  |
| 14 | Cross section of each wire | mm2 |  |  |
| 15 | No.& diameter of wire in each conductor | No./mm |  |  |
| 16 | Class of Stranding |  | Class 2 |  |
| 17 | Operating Capacitance | µF/km |  |  |
| 18 | Maximum Conductor Temperature | °C | 90 |  |
| 19 | Conductor screen material |  |  |  |
| 20 | Thickness of Conductor Screen | mm | 0.6 |  |
| 21 | Thickness of XLPE insulation | mm | 3.4 |  |
| 22 | Insulation screen material |  |  |  |
| 23 | Thickness of Insulation Screen | mm | 0.7 |  |
| 24 | Water Swellable tape | Yes/No | Yes |  |
| 25 | Copper tape along with copper wire | Yes/No | Yes |  |
| 26 | Thickness of Copper Screen | mm | 0.1 |  |
| 27 | Nominal Thickness of PVC Inner sheath | mm |  |  |
| 28 | Copper Screen with water tight design | Yes/No | Yes |  |
| 29 | Armour Material and thickness |  |  |  |
| 30 | Nominal Thickness of HDPE Outer Sheath | Mm |  |  |
| 31 | Overall Diameter of the Cable | Mm |  |  |
| 32 | Continuous current rating at 45 deg. C. ambient |  |  |  |
|  | - in ground | A |  |  |
|  | - in duct | A |  |  |
| 33 | Short circuit current |  |  |  |
|  | - 0.1 sec | kA |  |  |
|  | - 1.0 sec (minimum kA) | kA |  |  |
| 34 | Electrical parameter |  |  |  |
|  | - Resistance/km |  |  |  |
|  | - Reactance/km |  |  |  |
|  | - Capacitance/km |  |  |  |
| 35 | Max. Partial Discharge |  |  |  |
| 36 | AC Test Voltage for 5 min. | kV |  |  |
| 37 | Insulation Level: |  |  |  |
|  | -Power frequency Withstand Voltage | kV |  |  |
|  | -Impulse Withstand, Crest | kV |  |  |
| 38 | Min. Insulation Resistance | Ohms |  |  |
| 39 | Max. Conductor DC Resistance at 20 Deg. C | Ohm/km |  |  |
| 40 | Geometric Mean Radius (GMR) of the Cable/Conductor | Mm |  |  |
| 41 | Fire resistance treated | Yes/No |  |  |
| 42 | Is manufacturer an ISO 9001 holder? | Yes/No | Yes |  |
| 43 | ISO 9001 (with design) certificate submitted? | Yes/No | Yes |  |
| 44 | Type test certificate submitted? | Yes/No | Yes |  |
| 45 | User's certificate submitted? | Yes/No | Yes |  |
| 46 | Standard drum length | Meter |  |  |
| 47 | Approx. Net Weight per Meter of cable | Kg |  |  |
| 48 | Net weight of cable in drum | Kg |  |  |
|  | Straight Through Joint |  |  |  |
| 49 | Manufacturer and Country of Origin |  |  |  |
| 50 | Year of manufacturing experience | Years | 10 |  |
| 51 | Catalogue Number |  |  |  |
| 52 | Copies of Governing Standards Attached |  | Yes |  |
| 53 | Applicable standard |  | IEC |  |
| 54 | Copies of type test attached | Yes/No | Yes |  |
| 55 | Type |  |  |  |
| 56 | Is Splice Kit Performed or Tape |  |  |  |
| 57 | Splicing voltage level | kV | 12 |  |
| 58 | Power frequency withstand voltage | kV | 21 |  |
| 59 | Impulse withstand voltage (BIL) | KV | 75 |  |
| 60 | Is ISO 9001 certificate submitted? | Yes/No | Yes |  |
| 61 | Technical literature/drawings submitted? | Yes/No | Yes |  |
| 62 | Embossing |  |  |  |

11 KV XLPE INSULATED ALL ALUMINIUM ALLOY CONDUCTOR (AAAC)

| No. | Description | Unit | NEA REQ. | DATA to be Filled 100 mm2 |
| --- | --- | --- | --- | --- |
| 1 | Manufacturer s Name & Address |  |  |  |
| 2 | Minimum Year of manufacturing experience | Years | 10 |  |
| 3 | List of Standard Applicable |  |  |  |
| 4 | Rated Voltage | kV | 11 |  |
| 5 | Conductors |  |  |  |
|  | a. Material |  | Aluminium |  |
|  | b. Actual Area | mm2 |  |  |
|  | c. Stranding & wire diameter | Nos / mm |  |  |
|  | d. Approximate overall diameter | mm |  |  |
|  | e. Approximate weight | kg/km |  |  |
|  | f. Maximum Calculated D.C. resistance at 20°C | Ohms/km |  |  |
|  | g. Approximate calculated breaking load | kN |  |  |
|  | h. Reactance |  |  |  |
|  | i. Current Rating | Amps |  |  |
|  | j. Lay ratio |  |  |  |
|  | k. Direction of lay |  |  |  |
| 6 | Wire (strand) used in the construction of conductors |  |  |  |
|  | a. Nominal Diameter | mm |  |  |
|  | b. Maximum Diameter | mm |  |  |
|  | c. Cross-section area of nominal diameter wire | mm2 |  |  |
|  | d. Weight | kg/km |  |  |
|  | e. Maximum Calculated D.C. resistance at 20°C |  |  |  |
|  | f. Minimum breaking load after stranding | kN |  |  |
| 7 | Insulation (Semi-conduction screen) |  |  |  |
|  | a. Material |  |  |  |
| 8 | Insulation (Inner layer) |  |  |  |
|  | a. Material |  | XLPE |  |
|  | b. Nominal thickness | mm |  |  |
|  | c. Carbon Content | % |  |  |
| 9 | Insulation (Outer layer) |  |  |  |
|  | a. Material |  |  |  |
|  | b. Nominal thickness | mm |  |  |
|  | c. Carbon Content | % |  |  |
| 10 | Combined insulation i.e. both layers |  |  |  |
|  | a. Minimum thickness | mm |  |  |
|  | b. Min. Tensile strength of insulation | N/mm2 |  |  |
|  | c. Elongation | min |  |  |
|  | - Volume resistivity - At room temperature of 027-cm) - At 70 -cm) |  |  |  |
|  | - Hot set - Max. Elongation underload - Max. Permanent elongation | % |  |  |
|  | f. AC Test Voltage for 5 min. | kV |  |  |
| 11 | Covered Conductor |  |  |  |
|  | a. Minimum Breaking Strength | kN |  |  |
|  | b. Short time current rating: 1 sec | kA |  |  |
|  | - c. Maximum conductor operating temperature - Continuous operation - Emergency operation - Short circuit operation; 5 sec | Deg C |  |  |
|  | d. Overall diameter (mm) |  |  |  |
|  | e. Approximate weight of complete cable | (kg/km) |  |  |
|  | - f. Maximum DC resistance of conductor at 20°C |  |  |  |
|  | g. Reactance |  |  |  |
| 12 | Size of cable drum |  |  |  |
| 13 | Approximate Length of conductor per drum (km ± %) |  |  |  |

MULTIPLE CORE LT XLPE ARMOURED CABLES.

| No. | PARTICULARS |  |  | LT XLPE armoured cable |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 3.5Cx300 | 3.5Cx185 | 3.5Cx95 |
| 1 | Manufacturer’s name and works address |  |  |  |  |  |
| 2 | Standard specification to which the material shall |  |  |  |  |  |
| 3 | VOLTAGE GRADE. |  |  |  |  |  |
| 4 | NO. OF CORES. |  |  |  |  |  |
| 5 | CONDUCTOR DETAILS: |  |  |  |  |  |
|  | A | Normal cross section area of : |  |  |  |  |
|  |  |  | Phase Conductor (Sq.mm) |  |  |  |
|  |  |  | Neutral Conductor (Sq.mm) |  |  |  |
|  | B | No. and size of strands (in mm) of: |  |  |  |  |
|  |  |  | Phase Conductor (Sq.mm) |  |  |  |
|  |  |  | Neutral Conductor (Sq.mm) |  |  |  |
|  | C | SHAPE OF CONDUCTOR |  |  |  |  |
|  | D | Whether compacted or non-compacted |  |  |  |  |
|  | E | DC Resistance at 20 0c |  |  |  |  |
|  |  |  | Phase Conductor ohm/km |  |  |  |
|  |  |  | Neutral Conductor ohm/km |  |  |  |
| 6 | INSULATION |  |  |  |  |  |
|  | 1 | Type |  |  |  |  |
|  | 2 | Colour |  |  |  |  |
|  | 3 | Thickness |  |  |  |  |
|  | A | Phase Conductor (sq.mm) |  |  |  |  |
|  |  |  | Nominal (mm) |  |  |  |
|  |  |  | Minimum (mm) |  |  |  |
|  | B | Neutral Conductor (Sq.mm) |  |  |  |  |
|  |  |  | Nominal (mm) |  |  |  |
|  |  |  | Minimum (mm) |  |  |  |
|  | C |  | Fictitious dia of core (mm) |  |  |  |
| 7 | Type of inner sheathing and colour |  |  |  |  |  |
|  | Fictitious dia over laid up cores |  |  |  |  |  |
|  | Thickness of inner sheath |  |  |  |  |  |
|  | Fictitious dia over inner sheath |  |  |  |  |  |
| 8 | Whether Binder Tape provided |  |  |  |  |  |
| 9 | Armoring |  |  |  |  |  |
|  | A | Type |  |  |  |  |
|  | B | Dimension (mm) |  |  |  |  |
|  | C | Fictitious dia over armour |  |  |  |  |
| 10 | Outer Sheath |  |  |  |  |  |
|  | A | Material |  |  |  |  |
|  | B | Thickness |  |  |  |  |
|  |  |  | Nominal (mm) |  |  |  |
|  |  |  | Minimum (mm) |  |  |  |
|  | C | Standard to which it Confirm |  |  |  |  |
| 11 | A | Type and size of filler used |  |  |  |  |
|  | B | Min. Wt. Of filler in KG./KM |  |  |  |  |
| 12 | Approx. Overall diameter of the cable in mm. |  |  |  |  |  |
| 13 | Nature of Packing. |  |  |  |  |  |
| 14 | DRUM |  |  |  |  |  |
|  | A | Tare weight of drum |  |  |  |  |
|  | B | Standard specification |  |  |  |  |
|  | C | Drum details & dimensions |  |  |  |  |
|  | D | Whether 2-Full Ply Flange Construction or 2-Full Ply plus 1 Segmental layer Flange Construction. |  |  |  |  |
| 15 | Embossing |  |  |  |  |  |

LT XLPE ARMOURED SERVCIE CABLES

| No. | PARTICULARS |  |  | Service cable |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 2Cx6 | 2Cx10 | 2Cx35 | 3Cx25+16 | 3Cx70+35 |
| 1 | Manufacturer’s name and works |  |  |  |  |  |  |  |
| 2 | Standard specification to which the material shall confirm |  |  |  |  |  |  |  |
| 3 | Voltage Grade. |  |  |  |  |  |  |  |
| 4 | No. Of Cores. |  |  |  |  |  |  |  |
| 5 | Conductor Details: |  |  |  |  |  |  |  |
|  | A | Normal cross section area of : |  |  |  |  |  |  |
|  |  |  | Phase Conductor (Sq.mm) |  |  |  |  |  |
|  |  |  | Neutral Conductor (Sq.mm) |  |  |  |  |  |
|  | B | No. and size of strands (in |  |  |  |  |  |  |
|  |  |  | Phase Conductor (Sq.mm) |  |  |  |  |  |
|  |  |  | Neutral Conductor(Sq.mm) |  |  |  |  |  |
|  | C | SHAPE OF CONDUCTOR |  |  |  |  |  |  |
|  | D | Whether compacted or non- compacted |  |  |  |  |  |  |
|  | E | DC Resistance at 20 0c |  |  |  |  |  |  |
|  |  |  | Phase Conductor ohm/km |  |  |  |  |  |
|  |  |  | Neutral Conductor ohm/km |  |  |  |  |  |
| 6 | INSULATION |  |  |  |  |  |  |  |
|  | 1 | Type |  |  |  |  |  |  |
|  | 2 | Colour |  |  |  |  |  |  |
|  | 3 | Thickness |  |  |  |  |  |  |
|  | A | Phase Conductor (sq.mm) |  |  |  |  |  |  |
|  |  |  | Nominal (mm) |  |  |  |  |  |
|  |  |  | Minimum (mm) |  |  |  |  |  |
|  | B | Neutral Conductor (Sq.mm) |  |  |  |  |  |  |
|  |  |  | Nominal (mm) |  |  |  |  |  |
|  |  |  | Minimum (mm) |  |  |  |  |  |
|  | C | Fictitious dia of core (mm) |  |  |  |  |  |  |
| 7 | Type of inner sheathing and colour |  |  |  |  |  |  |  |
|  | Fictitious dia over laid up cores |  |  |  |  |  |  |  |
|  | Thickness of inner sheath |  |  |  |  |  |  |  |
|  | Fictitious dia over inner sheath |  |  |  |  |  |  |  |
| 8 | Whether Binder Tape provided |  |  |  |  |  |  |  |
| 9 | Armoring |  |  |  |  |  |  |  |
|  | A | Type |  |  |  |  |  |  |
|  | B | Dimension (mm) |  |  |  |  |  |  |
|  | C | Fictitious dia over armour |  |  |  |  |  |  |
| 10 | Outer Sheath |  |  |  |  |  |  |  |
|  | A | Material |  |  |  |  |  |  |
|  | B | Thickness |  |  |  |  |  |  |
|  |  |  | Nominal (mm) |  |  |  |  |  |
|  |  |  | Minimum (mm) |  |  |  |  |  |
|  | C | Standard to which it Confirm |  |  |  |  |  |  |
| 11 | A | Type and size of filler used |  |  |  |  |  |  |
|  | B | Min. Wt. Of filler in KG./KM |  |  |  |  |  |  |
| 12 | Approx. Overall diameter of the cable in mm. |  |  |  |  |  |  |  |
| 13 | Nature of Packing. |  |  |  |  |  |  |  |
| 14 | DRUM |  |  |  |  |  |  |  |
|  | A | Tare weight of drum |  |  |  |  |  |  |
|  | B | Standard specification |  |  |  |  |  |  |
|  | C | Drum details & dimensions |  |  |  |  |  |  |
|  | D | Whether 2-Full Ply Flange Construction or 2-Full Ply plus 1 Segmental layer Flange Construction. |  |  |  |  |  |  |
| 15 | Embossing |  |  |  |  |  |  |  |

11kV Outdoor Terminal Kit

|  | DESCRIPTION | UNIT | NEA REQ | DATA to be Filled |
| --- | --- | --- | --- | --- |
| 1 | Manufacturer and Country of Origin |  |  |  |
| 2 | Year of manufacturing experience | Years | 10 |  |
| 3 | Catalogue Number |  |  |  |
| 4 | Applicable standard |  | IEC |  |
| 6 | Type |  | Heat Shrinkable |  |
| 7 | Copies of type test Attached |  |  |  |
| 8 | Stress relief performed | Yes/No |  |  |
| 9 | Terminator insulation level | kV |  |  |
| 10 | Insulation Material |  | XLPE |  |
| 11 | Maximum design voltage | kV | 12 |  |
| 12 | Impulse withstand voltage (BIL) | kV |  |  |
| 13 | Installation Instruction attached | Yes/No | Yes |  |
| 14 | Fire resistance treated | Yes/No | Yes |  |
| 15 | Smoke resistance treated | Yes/No | Yes |  |
| 16 | Is ISO 9001 certificate submitted? | Yes/No | Yes |  |
| 17 | Technical literature/drawings submitted? | Yes/No | Yes |  |

HDPE PN6 PIPE (For HDD method)

|  | DESCRIPTION | UNIT | NEA REQ |  | DATA to be Filled |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 160mm dia | 125mm dia |  |
| 1 | Manufacturer and Country of Origin |  |  |  |  |
| 2 | Applicable standard |  |  |  |  |
| 3 | Type |  | HDPE PN6 | HDPE PN6 |  |
| 4 | PE grade |  |  |  |  |
| 5 | diameter of the pipe | mm |  |  |  |
| 6 | Wall Thickness | mm |  |  |  |
| 7 | Weight | kg/mtr |  |  |  |
| 8 | Technical Literature submitted | Yes/No | Yes | Yes |  |
| 9 | Type test certificate submitted | Yes/No | Yes | Yes |  |
| 10 | Technical literature/drawings | Yes/No | Yes | Yes |  |

HDPE PN4 PIPE (For open trench)

|  | DESCRIPTION | UNIT | NEA REQ |  | DATA to be Filled |
| --- | --- | --- | --- | --- | --- |
|  |  |  | 160mm dia | 125mm dia |  |
| 1 | Manufacturer and Country of Origin |  |  |  |  |
| 2 | Applicable standard |  |  |  |  |
| 3 | Type |  | HDPE PN4 | HDPE PN4 |  |
| 4 | PE grade |  |  |  |  |
| 5 | diameter of the pipe | mm |  |  |  |
| 6 | Wall Thickness | mm |  |  |  |
| 7 | Weight | Kg/mtr |  |  |  |
| 8 | Technical Literature submitted | Yes/No | Yes | Yes |  |
| 9 | Type test certificate submitted | Yes/No | Yes | Yes |  |
| 10 | Technical literature/drawings | Yes/No | Yes | Yes |  |

11kV SF6 Extensible RMU

| No. | Description | NEA Requirement | Offered Data |
| --- | --- | --- | --- |
| 1 | SWITCHGEAR ASSEMBLY |  |  |
| 1.1 | Name of Manufacturer |  |  |
| 1.2 | Country or Origin |  |  |
| 1.3 | Year of Manufacturing Experience | 10 Years |  |
| 1.4 | Make | Manufacturer to give details |  |
| 1.5 | Type | Outdoor |  |
| 1.6 | Reference Standard | IEC 56, IEC129, IEC298, IEC694, IEC 265 |  |
| 1.7 | Voltage (Normal/Max.) kV | 10kV/12 kV |  |
| 1.8 | Phase (Nos.) | 3 nos |  |
| 1.9 | Frequency (HZ) | 50 ± 3 Hz |  |
| 1.10 | Short Circuit rating |  |  |
|  | a) Breaking Symmetrical (KA) | 25 kA |  |
|  | b) Breaking Asymmetrical (KA) | 25 kA |  |
|  | c) Short time for 3 Sec. (KA) | 25 kA |  |
| 1.11 | Insulation Level |  |  |
|  | a) Impulse withstand (KV peak) | 75 kVp@1000mtr altitude |  |
|  | b) 1 Minute 50 Hz. Voltage withstand (KV rms) | 28 kVrms@1000mtr altitude |  |
| 1.12 | Metal Clad Construction | Yes |  |
| 1.13 | - Degree of protection for outer enclosure: - Degree of protection for main tank: | IP 54 IP 67 |  |
| 2 | CONSTRUCTION |  |  |
| 2.1 | Overall Dimensions | Mfg. to give details |  |
| 2.2 | Overall Weight of RMU Unit | Mfg. to give details |  |
| 3 | Bus bar | - | - |
| 3.1 | Make | Mfg. to give details |  |
| 3.2 | Material & Grade | Copper |  |
| 3.3 | Reference Standard | IEC 129 |  |
| 3.4 | - Cross sectional area (mm2) |  |  |
| 3.5 | Continuous Current |  |  |
|  | - a) Standard | 630 A |  |
|  | b) At site conditions and within cubicle | 630 A |  |
| 3.6 | Maximum temperature rise over ambient (c) | 55 °C (above ambient of 40 °C) |  |
| 3.7 | Short time current for 3 Sec. (kA) | 25 |  |
| 3.8 | Minimum clearance from bare bus bar | Mfg. to give details |  |
|  | a) Phase to phase (mm) |  |  |
|  | b) Phase to Earth (mm) |  |  |
| 3.11 | Bus Bar support spacing (mm) |  |  |
| 3.12 | Bus support insulators |  |  |
|  | - a) Make |  |  |
|  | - b) Type |  |  |
|  | c) Voltage Class (KV) |  |  |
|  | d) Minimum creepage distance (mm) |  |  |
|  | e) Cantilever strength Kg/mm2 |  |  |
| 3.13 | SF6 gas pressure (filing pressure at 20 deg. C) | Mfg. to give details |  |
| 4.0 | VCB CIRCUIT BREAKER |  |  |
| 4.1 | Make | Mfg. to give details |  |
| 4.2 | Type (Vacuum/ SF6) | Mfg. to give details |  |
| 4.3 | Reference Standard | IEC 56 |  |
| 4.4 | Rated Voltage | 11 kV |  |
| 4.5 | Rated Frequency | 50 Hz |  |
| 4.6 | No. Of Poles | 3 |  |
| 4.7 | Rated Current |  |  |
|  | a) Normal (Standard) Amps | 630A |  |
|  | b) Rated (Site) Amps | 630A |  |
| 4.8 | Maximum temperatures rise over ambient.(deg. C) | 55 °C (above ambient of 40 °C) |  |
| 4.9 | Rated operating Duty | O- 0.3Sec- CO-3min-CO |  |
| 4.10 | a) Short time current for 1 Sec.(KA rms) |  |  |
|  | b) Short time current for 3 Sec.(KA rms) |  |  |
| 4.11 | Transient Recovery Voltage |  |  |
|  | a) Rate of rise (KV/ms) | 0.34 KV/micro sec (as per IEC) |  |
|  | b) Peak Voltage (KV) |  |  |
| 4.12 | Opening time Maximum No load condition (ms) | 40-60 |  |
| 4.13 | Opening and closing time under SF6 gas loss or vacuum loss condition (ms) | 40-60 |  |
| 4.14 | At 100% Breaking capacity |  |  |
|  | a) Opening time – max (ms) | 40-60 |  |
|  | b) Arcing time – max (ms) | 6-9 |  |
|  | c) Total break time (ms) | 40-60 |  |
| 4.15 | At 60% Breaking capacity |  |  |
|  | a) Opening time – max (ms) | 40-60 |  |
|  | b) Arcing time – max (ms) | 6-9 |  |
|  | c) Total break time (ms) | 40-60 |  |
| 4.16 | Number of breaks per pole | Single |  |
| 4.17 | No of breaker operations permissible without requiring inspection replacement of contacts and other main parts. |  |  |
|  | At 100% rated breaking current |  |  |
| 4.18 | Type of contacts |  |  |
|  | a) Main | Copper chromium, Butt type |  |
|  | b) Arcing | Copper chromium |  |
| 4.19 | Material of contacts |  |  |
|  | a) Main | Copper chromium |  |
|  | b) Arching | Copper chromium |  |
|  | c) Whether contacts silver plated | NA |  |
|  | d) Thickness of silver plating | NA |  |
| 4.20 | Operating mechanism- closing |  |  |
|  | a) Type | Stored Energy |  |
|  | b) No of breaker operations stored | One Trip free |  |
|  | c) Trip free or fixed trip |  |  |
|  | d) Anti pumping features provided |  |  |
|  | e) Earthing for operating mechanism and metal parts furnished | Mfg. to give details |  |
|  | f) Earth terminal size and material | Mfg. to give details |  |
| 4.21 | Operating mechanism- tripping |  |  |
|  | a) Type | Mfg. to give details |  |
|  | b) No of breaker operations stored | One |  |
|  | c) Trip free or fixed trip (V) | Trip free |  |
|  | d) Anti pumping features provided (%) | NA |  |
|  | e) Earthing for operating mechanism and metal parts furnished | Mfg. to give details |  |
|  | f) Earth terminal size and material |  |  |
| 4.22 | Spring charging mechanism |  |  |
|  | a) Make |  |  |
|  | b) Type |  |  |
|  | c) Size |  |  |
|  | d) Rating |  |  |
| 4.23 | Breaker suitable for capacity switching 4 operating duty 5Max. rating of capacitor bank that can be safely controlled |  |  |
| 4.24 | Tripping coil |  |  |
|  | a) Voltage |  |  |
|  | b) Permissible voltage variation (%) |  |  |
|  | c) Tripping current at rated voltage |  |  |
|  | d) Power at rated voltage (W) |  |  |
|  | e) 2-Over current trip with TLF (5A) and 1-earth fault furnished as specified |  |  |
| 4.25 | Breaker/Accessories such as control switch indication Lamps etc. furnished as specified :(please attach separate sheet giving details of all accessories, interlocks and safety shutters) |  |  |
|  | a) Mechanical safety Interlock | Yes |  |
|  | b) Automatic Safety Interlock | No |  |
|  | c) Operational Interlock | Yes |  |
|  | d) Emergency manual trip | Yes |  |
|  | e) Operation counter | Yes |  |
|  | f) Charge /discharge indicator | Yes |  |
|  | g) Manual spring charging facility | Yes |  |
| 4.26 | Impact load foundation design (to include dead load plus impact value on opening at maximum interrupting rating) (Kg) | Mfg. to give details |  |
| 4.27 | Electrical class | E2 |  |
| 4.28 | Mechanical class | M1 |  |
| 5.0 | Isolators |  |  |
| 5.1 | Make | Mfg. to give details |  |
| 5.2 | Type | Mfg. to give details |  |
| 5.3 | Reference standard | IEC129 |  |
| 5.4 | Rated voltage (KV) | 12 |  |
| 5.5 | Rated Frequency Hz | 50 |  |
| 5.6 | No. Of poles (No) | 3 |  |
| 5.7 | Rated current |  |  |
|  | Normal (Standard) Amps | 630 |  |
|  | Derated (site) Amp | 630 |  |
| 5.8 | Maximum temperature rise over ambient Deg. C | 55 °C (above ambient of 40 °C) |  |
| 5.9 | Rated operation duty |  |  |
| 5.10 | Rupturing Capacity at rated voltage MVA | Mfg. to give details |  |
| 5.11 | Rated making current KA peak | Mfg. to give details |  |
| 5.12 | Short time current |  |  |
|  | a) For 1 sec KA rms | 20 |  |
|  | b) For 3 sec KA rms | 20 |  |
| 5.13 | Impulse voltage withstand on 1/50 full Wave | 75@1000mtr altitude |  |
| 5.14 | Maximum over voltage factor when switching off a) Loaded feeder cable | Mfg. to give details |  |
| 5.15 | Operating SF6 Gas pressure |  |  |
| 5.16 | No of isolator operation permissible without requiring inspection, replacement of contacts and other main parts At 100% rated current At 100% rated breaking current |  |  |
| 5.17 | Isolator provided with the following Mechanical safety Mechanical ON, OFF, CABLE EARTH indicators Operation counter Manual spring charging facility | Yes |  |
| 5.18 | Impact load for foundation design (To include dead load plus impact Values on opening at maximum interrupting rating) Kg | Mfg. to give details |  |
| 6.0 | CURRENT TRANSFORMER |  |  |
| 6.1 | Make | Mfg. to give details |  |
| 6.2 | Type & voltage level | Mfg. to give details |  |
| 6.3 | Reference standard | IEC 298 |  |
| 6.4 | C.T. ratio as specified | 100-50/1 A |  |
| 6.5 | Rated frequency | 50 |  |
| 6.6 | Short circuit withstand Short time current for 1 sec. kA rms Short time current for 3 sec. KA rms Dynamic current KA peak | Mfg. to give details |  |
| 6.7 | Class of insulation | Mfg. to give details |  |
| 6.8 | Temperature rises over ambient. Deg. C |  |  |
| 6.9 | Basic insulation level |  |  |
| 6.10 | For tripping CT RATIO Class of accuracy |  |  |
|  | Rated Burden VA |  |  |
|  | Knee Point Voltage V |  |  |
|  | Excitation Current at Vk/2 Amps |  |  |
|  | Rated Saturating Current Amps |  |  |
|  | Over Current Rating |  |  |
|  | Continuous % Over Load % |  |  |
| 7.0 | Cable terminations |  |  |
| 7.1 | Circuit Breaker |  |  |
|  | Type |  |  |
|  | Materials |  |  |
|  | Dimensions |  |  |
|  | Size |  |  |
|  | Height of Cable box from ground Level |  |  |
|  | Arrangement for supplying bus end cable box furnished for extensible ring main Unit | Mfg. to give details |  |
|  | Arrangement for mounting an extra cable box on each equipment furnished |  |  |
| 7.2 | Isolator |  |  |
|  | Type |  |  |
|  | Materials |  |  |
|  | Dimensions |  |  |
|  | Size |  |  |
|  | Height of Cable box from ground Level |  |  |
|  | Arrangement for supplying bus end cable box furnished for extensible ring main Unit |  |  |
|  | Arrangement for mounting an extra cable box on each equipment furnished | Mfg. to give details |  |
| 8.0 | Name Plate |  |  |
| 8.1 | Material |  |  |
| 8.2 | Thickness |  |  |
| 8.3 | Size for |  |  |
|  | Breaker Cubicle |  |  |
|  | Instruments / Devices |  |  |
| 9.0 | Painting |  |  |
| 9.1 | Finish of Breaker |  |  |
|  | Inside |  |  |
|  | Outside |  |  |
| 9.2 | Finish of Isolator |  |  |
|  | Inside |  |  |
|  | Outside |  |  |
| 10.0 | Drawing / Data |  |  |
| 10.1 | General arrangement for Panel Board | Mfg. to give details |  |
|  | Arrangement for mounting an extra cable box on each equipment furnished |  |  |

LT Feeder Panel with MuLti-FunctionAL Meter

| No. | Parameter Name | NEA requirement | Offered Data |
| --- | --- | --- | --- |
| 1. | Name or Trademark of Manufacturer. |  |  |
| 2. | Type of L.T. Pillar |  |  |
| 3. | Rated normal voltage |  |  |
| 4. | Material of construction of L. T. Pillar enclosure& doors |  |  |
| 5. | Thickness of M.S. sheet for enclosure |  |  |
| 6. | Thickness of sheet for doors |  |  |
| 7. | Color of the L. T. Pillar enclosure |  |  |
| 8. | Dimensions of cubicle without rain hood – Width x Depth x Height (in mm) |  |  |
| 9. | Dimensions of rain hood – Width x Depth x Height of centre lift (in mm) |  |  |
| 10. | Ingress Protection | IP-55 |  |
| 11. | Type of locking arrangements |  |  |
| 12. | Details of painting |  |  |
| 13. | Dimensions and details of asbestos sheets |  |  |
| 14. | Bus Bar |  |  |
|  | - Size of bus bar |  |  |
|  | - Size of neutral bus bar |  |  |
|  | - Grade and specification of material of Bus bars |  |  |
|  | - Rated normal current of Bus bars |  |  |
|  | - Rated safe temperature of Bus bars |  |  |
| 15. | No. of incoming and type of incoming |  |  |
| 16. | No. of outgoing and types of outgoing |  |  |
| 17. | Multi-Functional Meter | - | - |
|  | - Make & Type |  |  |
|  | - Rated Voltage |  |  |
|  | - Rated Current |  |  |
|  | - Rated Frequency (Hz) | 50Hz |  |
|  | - Accuracy | 0.5 S |  |
|  | - Communication Method | GPRS |  |
| 18. | GPRS modem | - | - |
|  | - Rated Voltage | 3 phase AC 77 to 470 V or 1 phase AC 230 V |  |
|  | - Power Supply Unit | Drawn from meter input |  |
|  | - Average Power Consumption under idle and during data transfer | Not more than 3.5 VA |  |
|  | - Withstand Capacity | 6.0 kV |  |
|  | - Operating Frequency Bands | GSM 900/1800 MHz |  |
|  | - Applicable Standards | ETSI GSM Phase 2+ Standard |  |
|  | - Short Message Service (SMS) | Yes |  |
|  | - Internet Services | TCP, UDP, HTTP, FTP |  |
|  | - Communication Interface | R2S32 Serial Link |  |
|  | - Maximum baud rate | 115,200 bauds |  |
|  | - RS232 Output Connector | 9 pin female/ RJ11 |  |
| 19 | SIM Card | - | - |
|  | - Operating Voltage of Interface | 1.8V/3V |  |
|  | - Applicable Standard for ESD | IEC61000-4-2 |  |

11m Steel Tubular Pole

| No. | Description | Unit | NEA Requirement | To be filled by Bidder/ Manufacturer |
| --- | --- | --- | --- | --- |
| 1 | Manufacturer |  |  |  |
|  | Country of Origin |  |  |  |
| 2 | Years of Manufacturing Experience | Years | 10 |  |
| 3 | Governing Standard for Tubing, Manufacturing and Testing |  |  |  |
| 4 | Are the poles fully Galvanized? | Yes/No | Yes |  |
| 5 | Governing Standard for Galvanization |  | ISO 1461 or IS:4736 or an equivalent international standard |  |
| 6 | Number of Sections | Number | 3 |  |
| 7 | Overall Length | M | 11 |  |
| 8 | Pole Designation |  | 410 SP-57 |  |
| 9 | Section Length |  |  |  |
| 9.1 | Top (h1) | M | 2.7 |  |
| 9.2 | Middle (h2) | M | 2.7 |  |
| 9.3 | Bottom (h3) | M | 5.6 |  |
| 10 | Outside Diameter |  |  |  |
| 10.1 | Top (h1) | Mm | 139.7 |  |
| 10.2 | Middle (h2) | Mm | 165.1 |  |
| 10.3 | Bottom (h3) | Mm | 193.7 |  |
| 11 | Thickness |  |  |  |
| 11.1 | Top (h1) | Mm | 4.5 |  |
| 11.2 | Middle (h2) | Mm | 4.85 |  |
| 11.3 | Bottom (h3) | Mm | 5.90 |  |
| 12 | Crippling Load | Kgf | 552 |  |
| 13 | Approximate Weight (excluding the weight of galvanization, base plate and pole cap) | Kg | 256 |  |
| 14 | Application of load from top of pole | M | 0.6 |  |
| 15 | Planting Depth | M | 1.8 |  |
| 16 | Delivery of equipment following award of contract and approval of drawing | Months |  |  |
| 17 | ISO 9001 holder (including design) | Yes/No | Yes |  |
| 17.1 | Submission of ISO 9001 certificate | Yes/No | Yes |  |
| 18 | Submission of Type test certificate | Yes/No | Yes |  |
| 18.1 | Submitted for the required ratings | Yes/No |  |  |
| 18.2 | Type test certified by |  |  |  |
| 19 | Submission of User's certificate | Yes/No | Yes |  |
| 20 | Experience of exporting to third country | Yes/No | Yes |  |
| 21 | Outline Drawings and associated GA attached | Yes/No | Yes |  |

9m Steel Tubular Pole

| No. | Description | Unit | NEA Requirement | To be filled by Bidder |
| --- | --- | --- | --- | --- |
| 1 | Manufacturer |  |  |  |
|  | Country of Origin |  |  |  |
| 2 | Years of Manufacturing Experience | Years | 10 |  |
| 3 | Governing Standard for Tubing, Manufacturing and Testing |  |  |  |
| 4 | Full Galvanization | Yes/No | Yes |  |
| 5 | Governing Standard for Galvanization |  | EN ISO 1461 or IS:4736 or an equivalent international standard |  |
| 6 | Number of Sections | Number | 3 |  |
| 7 | Overall Length | M | 9 |  |
| 8 | Pole Designation |  | 410 SP-33 |  |
| 9 | Section Length | - | - | - |
|  | - Top (h1) | M | 2.0 |  |
|  | - Middle (h2) | M | 2.0 |  |
|  | - Bottom (h3) | M | 5.0 |  |
| 10 | Outside Diameter | - | - | - |
|  | - Top (h1) | Mm | 114.3 |  |
|  | - Middle (h2) | Mm | 139.7 |  |
|  | - Bottom (h3) | Mm | 165.1 |  |
| 11 | Thickness | - | - | - |
|  | - Top (h1) | Mm | 3.65 |  |
|  | - Middle (h2) | Mm | 4.50 |  |
|  | - Bottom (h3) | Mm | 5.4 |  |
| 12 | Crippling Load | Kgf | 435 |  |
| 13 | Approximate Weight (excluding the weight of galvanization, base plate and pole cap) | Kg | 164 |  |
| 14 | Application of load from top of pole | M | 0.3 |  |
| 15 | Planting Depth | M | 1.5 |  |
| 16 | Delivery of equipment following award of contract and approval of drawing | Months |  |  |
| 17 | ISO 9001 holder (including design) | Yes/No | Yes |  |
| 17.1 | Submission of ISO 9001 certificate | Yes/No | Yes |  |
| 18 | Submission of Type test certificate | Yes/No | Yes |  |
| 18.1 | Submitted for the required ratings | Yes/No |  |  |
| 18.2 | Type test certified by |  |  |  |
| 19 | Submission of User's certificate | Yes/No | Yes |  |
| 20 | Experience of exporting to third country | Yes/No | Yes |  |
| 21 | Outline Drawings and associated GA attached | Yes/No | Yes |  |

Gang Operated SWitch

| No. | Description | Unit | NEA requirement | To be filled by Bidder |
| --- | --- | --- | --- | --- |
| 1 | Manufacturer |  |  |  |
| 2 | Country of Origin |  |  |  |
| 3 | Model No. |  |  |  |
| 4 | Year of manufacturing experience | Years |  |  |
| 5 | Applicable Standards |  | IEC |  |
| 6 | Type |  | Outdoor, Gapless, Zinc Oxide |  |
| 7 | Rated Voltage | kV | 12 |  |
| 8 | Rated Frequency | Hz | 50 |  |
| 9 | Current Carrying Capacity | A |  |  |
| 10 | Rated short time current | kA |  |  |
| 11 | Rated peak withstand current | kA |  |  |
| 12 | Rated line-charging breaking current | A |  |  |
| 13 | Rated Cable charging breaking Capacity | A |  |  |
| 14 | Number of Post Per Phase | Nos. |  |  |
| 15 | Minimum Creepage Distance | mm |  |  |
| 16 | Phase to Phase Clearance | mm | 600 |  |
| 17 | Phase to Earth Clearance | mm |  |  |
| 18 | Minimum distance between post insulator | mm | 550 |  |
| 19 | Number of Poles | Nos. | 3 |  |
| 20 | Number of Position | Nos. | 2 |  |
| 21 | One Minute Power Frequency withstand Voltage (Dry and Wet) | kV |  |  |
| 22 | Number of Nuts and Bolts for Current Carrying Connector | Nos |  |  |
| 23 | Maximum Current Density | A/mm | 1.6 |  |
| 24 | Minimum Cross Section for Current Carrying fixed contact | Sq.mm |  |  |
| 25 | Length of post insulator arm | mm |  |  |
| 26 | Size of Post Insulator arm | mm |  |  |
| 27 | Operating Pipe outer Dia. | mm | 32 |  |
| 28 | Operating Pipe inner Dia. | mm | 25 |  |
| 29 | Length of Operating Pipe (minimum) | m | 4 |  |
| 30 | Length of male contact on each side | mm |  |  |
| 31 | Thickness of male contact | mm |  |  |
| 32 | Width of male contact | mm |  |  |
| 33 | Angle between male contact | Deg. | 120 to 150 |  |
| 34 | Length of female contact | mm |  |  |
| 35 | Thickness of female contact | mm |  |  |
| 36 | Width of female contact | mm |  |  |

Lightning Arrestor

| No. | Description | Unit | NEA requirement | To be filled by Bidder |
| --- | --- | --- | --- | --- |
| 1 | Manufacturer |  |  |  |
| 2 | Country of Origin |  |  |  |
| 3 | Model No. |  |  |  |
| 4 | Year of manufacturing experience | Years |  |  |
| 5 | Applicable Standards |  | IEC |  |
| 6 | Type |  | Outdoor, Gapless, Zinc Oxide |  |
| 7 | Voltage rating of LA | kV | 9 |  |
| 8 | Nominal Discharge Current | kA | 10 |  |
| 9 | Surge counter with insulating base furnished | Yes/No | NA |  |
| 10 | Minimum power frequency spark over voltage | kV |  |  |
| 11 | Maximum 1/50 impulse spark over voltage | kV |  |  |
| 12 | Maximum front wave spark over voltage | kV |  |  |
| 13 | Maximum switch surge spark over voltage | kV |  |  |
| 14 | Number of section per pole |  |  |  |
| 15 | Insulation level | kV |  |  |
| 15.1 | Impulse withstand voltage (peak) | kV | 75 @ 1000m altitude |  |
| 15.2 | Power frequency withstand voltage (1min rms) | kV | 28 @ 1000m altitude |  |
| 16 | Creepage distance | mm | 360 |  |
| 17 | Earth terminal and accessories provided | Yes/No | Yes |  |
| 18 | Surge counter | Yes/No | NA |  |
| 19 | ISO 9001 holder | Yes/No | Yes |  |
| 20 | ISO 9001 certificate submitted | Yes/No | Yes |  |
| 21 | Type test certificate submitted | Yes/No | Yes |  |

Pole Clamps

| No. | Description | Unit | NEA requirement | To be filled by Bidder |
| --- | --- | --- | --- | --- |
| 1 | Manufacturer |  |  |  |
| 2 | Country of Origin |  |  |  |
| 3 | Model No. |  |  |  |
| 4 | Steel Classification |  |  |  |
|  | Governing Standard for galvanization |  |  |  |
| 5 | Drawing of Pole Clamp furnished |  |  |  |

Earth Rods and Clamps

| No. | Description | Unit | NEA requirement | To be filled by Bidder |
| --- | --- | --- | --- | --- |
| 1 | Name of Manufacturer |  |  |  |
| 2 | Country of Origin |  |  |  |
| 3 | Model No. |  |  |  |
| 4 | Material Description furnished? | Yes/No | Yes |  |
| 5 | Governing Standard for galvanization |  |  |  |
| 6 | Governing Standard for manufacturing and testing |  |  |  |
| 7 | Applicable Standards |  |  |  |
| 8 | Catalogue/Dimension drawings attached for all items? | Yes/No | Yes |  |
| 9 | Dimensions (Ground Rod) |  |  |  |
|  | Length | mm |  |  |
|  | Diameter | Mm |  |  |
| 10 | Catalogue number |  |  |  |
|  | Rod |  |  |  |
|  | Clamp |  |  |  |

Grounding Conductor

| No. | Description | Unit | NEA requirement | To be filled by Bidder |
| --- | --- | --- | --- | --- |
| 1 | Manufacturer and Country of Origin Model No. |  |  |  |
| 2 | Governing Standard for manufacturing and testing |  |  |  |
| 3 | Governing Standard for galvanization |  |  |  |
| 4 | Standards attached? | Yes/No | Yes |  |
| 5 | Cross Section | sq. mm |  |  |
| 6 | Short time fusing 30 cycles | Amps |  |  |
| 7 | Weight (Approx) | kg/km |  |  |
| 8 | Length | mm |  |  |
| 9 | Resistance at 20 deg C (Approx) | ohms/km |  |  |

Galvanized Steel Nuts and Bolts

| No. | Description | Unit | NEA requirement | To be filled by Bidder |
| --- | --- | --- | --- | --- |
| 1 | Manufacturer |  |  |  |
| 2 | Country of Origin |  |  |  |
| 3 | Model No. |  |  |  |
| 4 | Material Description furnished? | Yes/No | Yes |  |
| 5 | Governing Standard for galvanization |  |  |  |
| 6 | Governing Standard for manufacturing and testing |  |  |  |
| 7 | Standards attached? | Yes/No | Yes |  |
| 8 | Catalogue/Dimension drawings attached for all items? | Yes/No | Yes |  |

High Voltage Warning/Danger Plate

| No. | Description | Unit | NEA requirement | To be filled by Bidder |
| --- | --- | --- | --- | --- |
| 1 | Manufacturer |  |  |  |
| 2 | Country of Origin |  |  |  |
| 3 | Model No. |  |  |  |
| 4 | Applicable Standard |  |  |  |
| 5 | Type of Material |  |  |  |
| 6 | Size |  |  |  |
| 7 | Submission of Technical literature/Drawing | Yes/No | Yes |  |

RTU (Remote Terminal Unit)

| No. | Description | NEA Requirement | To be filled by Bidder |
| --- | --- | --- | --- |
| 1 | Manufacturer |  |  |
|  | - Name of manufacturer |  |  |
|  | - Type |  |  |
|  | - Years of Manufacturing | 10 Years |  |
| 2 | Cabinet |  |  |
| 2.1 | Dimensions of cabinets (packs) completely equipped and wired |  |  |
|  | - Height (mm) | Less than 2100 mm |  |
|  | - Width (mm) |  |  |
|  | - Depth (mm) |  |  |
|  | - Weight (kg) |  |  |
| 2.2 | Maintainability of cabinet |  |  |
|  | - No preventive maintenance and inspections. | Yes/No |  |
|  | - If required. No medium or high voltage circuit be de-energized. | Yes |  |
| 2.3 | Corrosion Protection |  |  |
|  | - The surface shall be cleaned to bare material by mechanical or chemical means. | Yes |  |
|  | - One or more phosphatizing or priming coats of paint shall be applied to the bare surface using a zinc-based or lead-based primer. | Yes |  |
|  | - A finish coat with high scratch resistance or epoxy powder finish paint shall be applied over the primer. |  |  |
|  | - The coat thickness shall be no less than-as follows: |  |  |
|  | - Primer layer: Approx. 50 µm |  |  |
|  | - Intermediate layer (if necessary): Approx. 70 µm. |  |  |
|  | - Top coat (finish layer): Approx. 60 µm. |  |  |
|  | - Finish-coat Color | RAL 7032 shade |  |
| 2.4 | Ingress Protection | IP41 |  |
| 2.5 | Rodent Protection | Yes |  |
| 2.6 | Galvanizing |  |  |
| 2.7 | Marking |  |  |
| 3 | Main Module |  |  |
|  | - Manufacturer |  |  |
|  | - Model/Type |  |  |
|  | - Firmware version year |  |  |
|  | - RTOS maker, name, version |  |  |
| 3.1 | Central Processing Module (CPM) |  |  |
|  | - The processor shall provide diagnostic information in the message structure that the DMS shall monitor. A flag shall be set if the RTUs performs a restart for any reason including power failure. | Yes |  |
|  | - The programming language for RTU user applications shall comply with IEC 61131-3. | Yes |  |
|  | - The CPM (Central Processing Module) shall be programmable in a high-level language like C. The Authority shall be able to program the RTU, manage the RTU database, upload/download parameters and configuration setting from the FRTU test set | Yes |  |
| 4 | Power Supply |  |  |
|  | - Power supply voltage | DC 48V |  |
|  | - Power consumption | Not more than 100W |  |
| 5 | Immunity to Electrical Stress and Disturbance |  |  |
|  | - Minimum Insulation of Equipment |  |  |
| 5.1 | Type test |  |  |
|  | - Testing institutions Name |  |  |
|  | - Exposed Equipment |  |  |
|  | - Rated Insulation Voltage (IEC 60255-5, Table I) | 500 V |  |
|  | - Dielectric Test Voltage (IEC 60255-5, Table I(Clause 6)) | 2 kV rms |  |
|  | - Insulation Resistance Test: Required (IEC 60255-5, Clause 7) | Yes |  |
|  | - Impulse Voltage Test (IEC 60255-5, Clause 8) | 5 kV 1.2/50 μs 0.5 J |  |
| 5.2 | Controlled Exposure Equipment |  |  |
|  | - Rated Insulation Voltage (IEC 60255-5, Table I) | 60 V |  |
|  | - Dielectric Test Voltage (IEC 60255-5, Table I(Clause 6)) | 1 kV rms |  |
|  | - Insulation Resistance Test : Required (IEC 60255-5, Clause 7) | Yes |  |
|  | - Impulse Voltage Test (IEC 60255-5, Clause 8) | 5 kV 1.2/50 μs 0.5 J |  |
| 5.3 | Immunity from EMI, Radiated Disturbance, and Electrostatic Discharge |  |  |
|  | - High Voltage Impulse (IEC 60060-1) | 5 kV 0.5 J |  |
|  | - Electrical Disturbances (1 MHz Burst) (IEC 60255-22-1, class 3) |  |  |
|  | - CM (Common Mode) | 2.5 kV |  |
|  | - DM (Differential Mode) | 1 kV |  |
| 5.4 | Electrostatic Discharge Immunity: |  |  |
|  | - Air (IEC 61000-4-2, Level 3) | 8 kV |  |
|  | - Direct 61000-4-2, Level 3) | 6 kV |  |
|  | - Radiated Immunity: |  |  |
|  | - 80 MHz - 1 GHz (IEC 61000-4-3, Level 3) or |  |  |
|  | - 27-500 MHz (IEC 60255-22-3, Class 3) or |  |  |
|  | - 50 kHz - 1 GHz (IEC 61000-4-3, Class 3) or |  |  |
|  | - 10 V/m 2 W at 0.6 m (ENV 50204 (GSM), Level 3) |  |  |
| 5.5 | Fast Transient/Burst Immunity: |  |  |
|  | - (IEC 61000-4-4, Level 4) or |  |  |
|  | - 4 kV On power supply port |  |  |
|  | - 2 kV On I/O Signal data and control |  |  |
|  | - 4 kV (IEC 60255-22-4, Class 4) or |  |  |
|  | - 4-5 kV (ANSI/IEEE C37.90.1) |  |  |
|  | - Surge Immunity (IEC 61000-4-5, Level 4) | 2 kV/4 kV |  |
|  | - Conducted Immunity (IEC 61000-4-6, Level 3) | 10 V |  |
|  | - Power Frequency Magnetic Field Immunity (IEC 61000-4-8, Level 3) | 10 A/m |  |
|  | - Pulse Magnetic Field Immunity (IEC 61000-4-9, Level 5) | 100 A/m |  |
|  | - Damped Oscillatory Magnetic Field Immunity (IEC 61000-4-10, Level 4) | 30 A/m |  |
|  | - Oscillatory Transient Immunity: |  |  |
|  | - Ring Wave (IEC 61000-4-12, Level 3) | 2 kV |  |
|  | - Damped Oscillatory (IEC 61000-4-12, Level 3) | 2 kV |  |
| 6 | Safe Design |  |  |
| 6.1 | Fail Safe Design Basic |  |  |
|  | - Safe Default Operation | Yes |  |
| 6.2 | Redundancy: |  |  |
|  | - CPU | Yes |  |
|  | - power supplies | Yes |  |
|  | - communication interfaces | Yes |  |
| 6.3 | Watchdog Timer: | Yes |  |
|  | - Communication Monitoring and Timeout: | Yes |  |
|  | - Data Protection and Backup: | Yes |  |
|  | - Alarms and Notifications: | Yes |  |
|  | - Fail-Open/Fail-Close Design: | Yes |  |
|  | - Fail safe design Detail | Yes |  |
|  | - The probability of undetected bit errors is no greater than |  |  |
|  | - for data | 10-10 |  |
|  | - for control | 10-14 |  |
| 6.4 | Control output logic criteria |  |  |
|  | - No false output shall result from a single point of failure in any Card | Yes |  |
|  | - No false output shall result during power up or power down of the RTUs. | Yes |  |
|  | - No false output shall result from inadvertently inserting a circuit card into a wrong slot within the FRTUs. | Yes |  |
| 7 | Availability of diagnostic information |  |  |
| 7.1 | Hardware Monitoring |  |  |
|  | - Monitors CPU status |  |  |
|  | - Memory usage |  |  |
|  | - Power conditions |  |  |
|  | - I/O modules overload or disconnection |  |  |
| 7.2 | Communication Diagnostics |  |  |
|  | - Tracks communication health with other devices |  |  |
|  | - SCADA/DMS system in DCC |  |  |
|  | - SAS |  |  |
|  | - RMU/FRTU |  |  |
|  | - Packet errors and timeouts. |  |  |
| 7.3 | Signal Monitoring |  |  |
|  | - Monitors abnormalities of digital and analog input/output signals |  |  |
| 7.4 | Self-Diagnostics |  |  |
|  | - watchdog timers |  |  |
|  | - System logs, to automatically detect and recover from system hang-ups or malfunctions. |  |  |
|  | - Environmental Monitoring |  |  |
|  | - Monitors temperature and humidity |  |  |
|  | - Firmware Diagnostics |  |  |
|  | - Tracks firmware version and health, |  |  |
|  | - detecting any errors or issues |  |  |
| 8 | Maintainability |  |  |
| 8.1 | I/O Module |  |  |
|  | - Shall be replaceable without reprogramming, redefinition of configuration parameters, or rewiring | Yes |  |
|  | - A control disable switch shall be provide within each I/O module | Yes |  |
| 8.2 | Time and Date Facility |  |  |
|  | - Local GPS receiver | Yes |  |
|  | - Shall be synchronized using a GMT reference signal generated by the DMS in long format and properly accounting for relevant communication path delays | Yes |  |
|  | - The resolution of the internal clock | 1 ms or better |  |
|  | - Real-time synchronization accuracy | 1 ms |  |
|  | - The internal clock must be re-synchronized using the DMS time and date reference signal when the unit is powered up | Yes |  |
| 9 | Maintenance Tool (Portable Configuration and Maintenance Terminal, PCMT) (If required) |  |  |
| 9.1 | Remote Configuration Tool or Configuration Software |  |  |
|  | - Maintenance Tool Software |  |  |
|  | - Engineering (Configuration) Tool Software |  |  |
|  | - SCADA Configuration Utility Software |  |  |
| 9.2 | Hardware |  |  |
|  | - OS |  |  |
|  | - Maker |  |  |
|  | - Type/Model |  |  |
|  | - CPU |  |  |
|  | - Memory |  |  |
|  | - Storage |  |  |
| 10 | Input and Output |  |  |
| 10.1 | Functional Requirements |  |  |
|  | Onboard battery | Yes/No |  |
| 10.2 | Input/Out Points |  |  |
|  | - Number of DI point |  |  |
|  | - Number of DO point |  |  |
|  | - Number of AI point |  |  |
|  | - A/D converters, a digital resolution | at least 32,767 counts (sign plus 15 data bits) |  |
|  | - Number of AO point |  |  |
| 10.3 | Status Inputs (DI) |  |  |
|  | - input dry contact with power supplied from RTU | Yes |  |
|  | - The debounce time period for each status input shall be individually user configurable. | Yes |  |
|  | - Optical isolate | Yes |  |
|  | - LED indicator or LCD with keypad | Yes |  |
|  | - Wetting Voltage | 24~60 VDC |  |
|  | - Single Contact, Two-State Status (SC-2S) | Yes |  |
|  | - Double Contacts, Two-State Status (DC-2S) | Yes |  |
|  | - Pulse Accumulators | Yes |  |
| 10.4 | Control Outputs (DO) |  |  |
|  | - Dry Contact | Yes |  |
|  | - On/Off Device Control | Yes |  |
|  | - Momentary control outputs | Yes |  |
|  | - Pulse duration (adjustable) | 0.1 to 25 s |  |
|  | - Increment (pulse duration) | 0.1 s |  |
|  | - Command receipt timer (adjustable) | up to 20 s or longer |  |
|  | - Control output contacts Voltage | 24~130 VDC |  |
|  | - Control output contacts operations |  |  |
|  | - Control output relay driving load | 6 A at primary control voltage |  |
|  | - Select-Before-Operate (SBO) | Yes |  |
| 10.5 | Configurable Serial Ports |  |  |
|  | - Serial RS-232 ports | Yes |  |
|  | - Serial RS-485 ports | Yes |  |
|  | - for data communication with the DMS (1200-19200 bps) | 1 |  |
|  | - for local diagnostic and test purposes (1200-19200 bps) | 1 |  |
|  | - Protocol | MODBUS RTU |  |
| 11 | Communication port |  |  |
| 11.1 | Ethernet (IP) Communications |  |  |
|  | - Master Station via SDH/MPLS |  |  |
|  | - Protocol:60870-5-104 | Yes |  |
|  | - Port: Optical Ether Net | Yes |  |
|  | - SAS via GW(Gateway) |  |  |
|  | - Protocol:60870-5-104 | Yes |  |
|  | - Port: Optical Ether Net | Yes |  |
|  | - Maintenance PC (PCMT) |  |  |
|  | - Protocol: | Yes |  |
|  | - Port: Ether Net | Yes |  |
|  | - Local SCADA (if required) |  |  |
|  | - Protocol: | Yes |  |
|  | - Port: Optical Ether Net | Yes |  |
| 12 | Data Processing |  |  |
| 12.1 | Sequence of Events |  |  |
|  | - Assignation of any status input point to SOE point | Yes |  |
|  | - SOE resolution time of change | ±1ms or better |  |
|  | - SOE buffer sizing | At least 5,000 events |  |
|  | - Reporting SOE events | Yes |  |
| 12.2 | Scan Group |  |  |
|  | - Number of Scan Group | At least 16 group |  |
| 13 | Test |  |  |
| 13.1 | RTU Testing |  |  |
|  | - Test Plans and Test Procedures | Yes |  |
|  | - Test Report | Yes |  |
|  | - Factory Inspections and Test | Yes |  |
|  | - Type Testing | Yes |  |
|  | - The RTUs as a class, shall have passed type tests in accordance with IEC 60255-3, IEC 60255-5, IEC 60255-6, IEC 61000-4-2, and IEC 61000-4-3 | Yes |  |
|  | - Dielectric tests | Yes |  |
|  | - Impulse voltage withstand tests | Yes |  |
|  | - High frequency disturbance tests | Yes |  |
|  | - Thermal requirement tests | Yes |  |
|  | - Mechanical requirement tests | Yes |  |
|  | - Contact performance tests | Yes |  |
|  | - Electromagnetic radiation susceptibility tests | Yes |  |
|  | - Electrostatic discharge susceptibility tests | Yes |  |
| 13.2 | Factory Acceptance Test (FAT) |  |  |
|  | - Full Functional Test | Yes |  |
|  | - Factory Routine Test | Yes |  |
|  | - Test Procedure | Yes |  |
|  | - Factory Acceptance Test (FAT) Procedure including test circuit diagrams and Test Results Report Format | Yes |  |
| 13.3 | Site Acceptance Test (SAT) | Yes |  |
|  | - Site Acceptance Test (SAT) Procedure including test circuit diagrams and Test Results Report Format | Yes |  |
|  | - Switchgear operation Test | Yes |  |
|  | - End-to-End Test | Yes |  |
| 13.4 | Test Equipment list and Calibration Certificate | Yes |  |
| 14 | Documentation |  |  |
|  | - Documentation Plan | Yes |  |
|  | - Manuals | Yes |  |
|  | - Installation Manual |  |  |
|  | - User Manual |  |  |
|  | - Configuration Manual |  |  |
|  | - Maintenance Manual |  |  |
|  | - Troubleshooting Manual |  |  |
|  | - Technical Specifications Manual |  |  |
|  | - Software Update Guide |  |  |
|  | - Drawings | Yes |  |

FRTU (Feeder Remote Terminal Unit)

| Item | Details | NEA Requirement | To be filled by Bidder |
| --- | --- | --- | --- |
| 1 | FRTU module |  |  |
|  | - Manufacturer |  |  |
|  | - Model |  |  |
|  | - Firmware version year |  |  |
|  | - Years of Manufacturing | 10 Years |  |
| 2 | Common Specifications |  |  |
| 2.1 | Service Condition |  |  |
|  | - Operation at elevations | up to 1,500 meters above sea level. |  |
| 2.2 | Outdoor Devices |  |  |
| 2.2.1 | Type test |  |  |
|  | - Submission of Certified copy of type test certificates and test report | Yes |  |
|  | - Temperature (per IEC 60068-2-1, 2 and 3) | -10°C to +60°C |  |
|  | - Temperature Gradient (per IEC 60068-2-14) | up to 30°C |  |
|  | - Relative Humidity (per IEC 60068-2-30) | up to 95% at 40°C |  |
|  | - Cyclic Damp Heat (per IEC 60068-2-30) | 40°C to 25°C at 95% Relative Humidity |  |
|  | - Absolute Humidity (per IEC 60068-2-30) | up to 29 g/m3 |  |
|  | - Vibration (sinusoidal) (per IEC 60068-2-6) | 2 g acceleration, 9 to 350 Hz |  |
|  | - Shock test (per IEC 60068-2-27) | 15 g 11 ms |  |
|  | - For pole-mounted device | up to 10 degrees |  |
| 2.3 | Fail Safe Design |  |  |
|  | - The probability of undetected bit errors is no greater than |  |  |
|  | - for data | 10-10 |  |
|  | - for control | 10-14 |  |
| 2.4 | Control output logic criteria |  |  |
|  | - No false output shall result from a single point of failure in any Card | Yes |  |
|  | - No false output shall result during power up or power down of the FRTUs. | Yes |  |
|  | - No false output shall result from inadvertently inserting a circuit card into a wrong slot within the FRTUs. | Yes |  |
| 2.5 | Maintainability |  |  |
|  | - No preventive maintenance and inspections. | Yes/No |  |
|  | - If required. No medium or high voltage circuit be de-energized. | Yes |  |
| 2.6 | Ingress Protection | IP20, IP40 for front |  |
| 2.7 | Marking |  |  |
| 2.8 | Immunity to Electrical Stress and Disturbance | - | - |
| 2.8.1 | Minimum Insulation of Equipment | - | - |
|  | Type test | - | - |
|  | - Exposed Equipment: | - |  |
|  | - Rated Insulation Voltage (IEC 60255-5, Table I) | 500 V |  |
|  | - Dielectric Test Voltage (IEC 60255-5, Table I(Clause 6)) | 2 kVrms |  |
|  | - Insulation Resistance Test: Required (IEC 60255-5, Clause 7) | Yes |  |
|  | - Impulse Voltage Test (IEC 60255-5, Clause 8) | 5 kV 1.2/50 us 0.5 J |  |
|  | - Controlled Exposure Equipment: | - | - |
|  | - Rated Insulation Voltage (IEC 60255-5, Table I) | 60 V |  |
|  | - Dielectric Test Voltage (IEC 60255-5, Table I(Clause 6)) | 1 kVrms |  |
|  | - Insulation Resistance Test: Required (IEC 60255-5, Clause 7) | Yes |  |
|  | - Impulse Voltage Test (IEC 60255-5, Clause 8) | 5 kV 1.2/50 μs 0.5 J |  |
| 2.8.2 | Immunity from EMI, Radiated Disturbance, and Electrostatic Discharge |  |  |
|  | - High Voltage Impulse (IEC 60060-1) | 5 kV 0.5 J |  |
|  | - Electrical Disturbances (1 MHz Burst) (IEC 60255-22-1, class 3) |  |  |
|  | - CM (Common Mode) | 2.5 kV |  |
|  | - DM (Differential Mode) | 1 kV |  |
| 2.8.3 | Electrostatic Discharge Immunity |  |  |
|  | - Air (IEC 61000-4-2, Level 3) | 8 kV |  |
|  | - Direct 61000-4-2, Level 3) | 6 kV |  |
|  | - Radiated Immunity: | - | - |
|  | - 80 MHz - 1 GHz (IEC 61000-4-3, Level 3) or |  |  |
|  | - 27-500 MHz (IEC 60255-22-3, Class 3) or |  |  |
|  | - 50 kHz - 1 GHz (IEC 61000-4-3, Class 3) or |  |  |
|  | - 10 V/m 2 W at 0.6 m (ENV 50204 (GSM), Level 3) |  |  |
| 2.8.4 | Fast Transient/Burst Immunity: |  |  |
|  | - (IEC 61000-4-4, Level 4) or |  |  |
|  | - 4 kV On power supply port |  |  |
|  | - 2 kV On I/O Signal data and control |  |  |
|  | - 4 kV (IEC 60255-22-4, Class 4) or |  |  |
|  | - 4-5 kV (ANSI/IEEE C37.90.1) |  |  |
|  | - Surge Immunity (IEC 61000-4-5, Level 4) | 2 kV/4 kV |  |
|  | - Conducted Immunity (IEC 61000-4-6, Level 3) | 10 V |  |
|  | - Power Frequency Magnetic Field Immunity (IEC 61000-4-8, Level 3) | 10 A/m |  |
|  | - Pulse Magnetic Field Immunity (IEC 61000-4-9, Level 5) | 100 A/m |  |
|  | - Damped Oscillatory Magnetic Field Immunity (IEC 61000-4-10, Level 4) | 30 A/m |  |
|  | - Oscillatory Transient Immunity: |  |  |
|  | - Ring Wave (IEC 61000-4-12, Level 3) | 2 kV |  |
|  | - Damped Oscillatory (IEC 61000-4-12, Level 3) | 2 kV |  |
| 3 | Functional Requirements |  |  |
|  | - Onboard battery | No |  |
| 3.1 | Input/Out Points |  |  |
|  | - Number of DI point |  |  |
|  | - Number of DO point |  |  |
|  | - Number of AI point |  |  |
|  | - A/D converters, a digital resolution | at least 16 bits plus sign |  |
|  | - Number of AO point |  |  |
|  | - Communication port: | - | - |
|  | - Number of RS232 port |  |  |
|  | - Number of RS485 port |  |  |
|  | - Number of Ethernet Port |  |  |
|  | - Number of USB Port |  |  |
| 3.1.2 | Status Inputs | - | - |
|  | - The debounce time period for each status input shall be individually user configurable. | Yes |  |
|  | - Optical isolate | Yes |  |
|  | - LED indicator or LCD with keypad | Yes |  |
|  | - Wetting Voltage | 24 VDC |  |
|  | - Accommodated: | - | - |
|  | - Single Contact, Two-State Status (SC-2S) | Yes |  |
|  | - Double Contacts, Two-State Status (DC-2S) | Yes |  |
|  | - Pulse Accumulators | Yes |  |
| 3.1.3 | Control Outputs | - | - |
|  | - On/Off Device Control | Yes |  |
|  | - Momentary control outputs | Yes |  |
|  | - Pulse duration (adjustable) | 0.1 to 25 s |  |
|  | - Increment (pulse duration) | 0.1 s |  |
|  | - Command receipt timer (adjustable) | up to 20 s or longer |  |
|  | - Control output contacts Voltage | 24 VDC |  |
|  | - Control output contacts operations | 106 |  |
|  | - Control output relay driving load | 6 A at primary control voltage |  |
|  | - Select-Before-Operate (SBO) | Yes |  |
| 3.2 | Input/Out Points Counts |  |  |
| 3.3 | Sequence of Events: |  |  |
|  | - Assignation of any status input point to SOE point | Yes |  |
|  | - SOE resolution time of change | ±1ms or better |  |
|  | - SOE buffer sizing | At least 20,000 events |  |
| 3.4 | Feeder Fault Current Detection |  |  |
|  | - Detecting the passage of feeder fault current | Yes |  |
|  | - Capability to download and upload fault current setpoints and fault duration time periods | Yes |  |
|  | - Designed to prevent misoperation due to magnetizing-inrush current and other transient no-fault conditions | Yes |  |
|  | - Involving up to 3 reclosures prior to lockout | Yes |  |
|  | - Reporting SOE events | Yes |  |
|  | - Buffer | at least 128 events |  |
| 3.5 | Configurable Serial Ports |  |  |
|  | - Serial RS-232 ports | Yes |  |
|  | - Serial RS-485 ports | Yes |  |
|  | - for data communication with the DMS (1200-19200 bps) | 1 |  |
|  | - for local diagnostic and test purposes (1200-19200 bps) | 1 |  |
|  | - Protocol | MODBUS RTU |  |
| 3.6 | Master Station Communications |  |  |
|  | - 60870-5-104 | Yes |  |
| 4 | FRTU Architecture |  |  |
| 4.1 | Central Processing Module |  |  |
|  | - The processor shall provide diagnostic information in the message structure that the DMS shall monitor. A flag shall be set if the FRTUs performs a restart for any reason including power failure. | Yes |  |
|  | - Applied RTOS (Real Time Operation System) |  |  |
|  | - CPM shall be programmable in a high-level language like C. The Authority shall be able to program the FRTU, manage the FRTU database, upload/download parameters and configuration setting from the FRTU test set | Yes |  |
|  | - Watch dog timer | Yes |  |
| 4.2 | I/O Module |  |  |
|  | - Shall be replaceable without reprogramming, redefinition of configuration parameters, or rewiring | Yes |  |
|  | - A control disable switch shall be provided within each I/O module | Yes |  |
| 4.3 | Time and Date Facility |  |  |
|  | - Shall be synchronized using a GMT reference signal generated by the DMS in long format and properly accounting for relevant communication path delays | Yes |  |
|  | - The resolution of the internal clock | 1 ms or better |  |
|  | - Real-time synchronization accuracy | 1 ms |  |
|  | - The internal clock must be re-synchronized using the DMS time and date reference signal when unit is power up | Yes |  |
| 4.4 | Enclosures | Yes |  |
| 4.5 | Power Supply | Yes |  |
|  | - Voltage | 24 VDC |  |
|  | - Total burden (W) |  |  |
| 5 | FRTU Test Set |  |  |
| 6 | Software/Firmware |  |  |
| 6.1 | General |  |  |
| 6.2 | Diagnostic Software |  |  |
| 6.3 | Programmable Logic Facility |  |  |
| 7 | FRTU Testing |  |  |
| 7.1 | Testing | Yes |  |
| 7.2 | Test Plans and Test Procedures | Yes |  |
| 7.3 | Test Report | Yes |  |
| 7.4 | Factory Inspections and Test | Yes |  |
|  | - Type Testing | Yes |  |
|  | - The FRTUs as a class, shall have passed type tests in accordance with IEC 60255-3, IEC 60255-5, IEC 60255-6, IEC 61000-4-2, and IEC 61000-4-3 | Yes |  |
|  | - Dielectric tests | Yes |  |
|  | - Impulse voltage withstand tests | Yes |  |
|  | - High frequency disturbance tests | Yes |  |
|  | - Thermal requirement tests | Yes |  |
|  | - Mechanical requirement tests | Yes |  |
|  | - Contact performance tests | Yes |  |
|  | - Electromagnetic radiation susceptibility tests | Yes |  |
|  | - Electrostatic discharge susceptibility tests | Yes |  |
| 7.5 | Factory Acceptance Test |  |  |
| 7.5.1 | Full Functional Test | Yes |  |
| 7.5.2 | Factory Routine Test | Yes |  |
| 7.5.3 | Site Acceptance Test | Yes |  |
| 7.5.4 | End-to-End Test | Yes |  |
| 7.6 | Test Equipment | Yes |  |
| 8 | Documentation Plan | Yes |  |
| 8.1 | Instructor Manuals | Yes |  |
| 8.2 | Drawings | Yes |  |

SDH/MPLS Switchable Optical Terminal

| No. | Description | NEA Requirement | To be filled by Bidder |
| --- | --- | --- | --- |
| 1 | Manufacturer |  |  |
|  | - Name of manufacturer |  |  |
|  | - Type |  |  |
|  | - Power supply voltage | To apply the contractor supply 48Vdc system |  |
|  | - Consumption (W) |  |  |
| 2 | Installation and size |  |  |
|  | - To be installed in RTU cabinet |  |  |
|  | - 19 inch Lack mount type |  |  |
|  | - Size: W (width) x H (height) x D (depth) |  |  |
| 3 | Function |  |  |
|  | - Supported Protocols: |  |  |
|  | - SDH, MPLS, MPLS-TP (Transport Profile) | Ensures the equipment supports both SDH and MPLS protocols |  |
|  | - IEC607870-5-104 Protocol handling |  |  |
|  | - TCP/IP over SDH | Yes |  |
|  | - Encapsulation (VC-12, VC-4) | Yes |  |
|  | - Transmission Speed: |  |  |
|  | - Supported transmission speeds for both SDH and MPLS | STM-1, STM-4, STM-16, STM-64, 1Gbps, 10Gbps, 40Gbps, 100Gbps |  |
|  | - Cross-Connect Function |  |  |
|  | - Digital Cross Connect (DXC), Ethernet Cross Connect | Cross-connect functionality between SDH and MPLS |  |
|  | - SDH Layer Cross-connect | (TDM multiplexing at VC-12, VC-4 level) |  |
|  | - Protection Features |  |  |
|  | - MSP (Multiplex Section Protection), SNCP (Sub-Network Connection Protection), Fast Reroute | Protection features for both SDH and MPLS |  |
|  | - Synchronization |  |  |
|  | - SSU (Synchronization Supply Unit), SyncE (Synchronous Ethernet) | Synchronization support for both SDH and MPLS networks |  |
|  | - Label Switching Function |  |  |
|  | - Label Distribution Protocol (LDP), RSVP-TE | Label switching protocols for MPLS networks |  |
|  | - VPN Support |  |  |
|  | - L2VPN, L3VPN, VPLS | VPN support within the MPLS network |  |
|  | - Bandwidth Management |  |  |
|  | - Bandwidth Allocation, Traffic Engineering, Load Balancing | Bandwidth management, traffic engineering, and load balancing |  |
|  | - Service Interfaces |  |  |
|  | - Ethernet over SDH (EoS), Ethernet over MPLS (EoMPLS), TDM over MPLS | Support for Ethernet and TDM services over both SDH and MPLS |  |
|  | - Management Functions |  |  |
|  | - SNMP, CLI, Web Interface, Network Management System (NMS) | Management and monitoring support for both SDH and MPLS |  |
|  | - Security Features |  |  |
|  | - Access Control, Encryption, Authentication | Security features for both SDH and MPLS |  |
|  | - Applicable Standards |  |  |
|  | - ITU-T G.707, G.783, G.803, RFC 3031, RFC 4364 | Compliance with standards for both SDH and MPLS |  |
|  | - Scalability Architecture, Multi-Protocol Support |  |  |
|  | - Scalability to accommodate future upgrades and protocol transitions from SDH to MPLS |  |  |
|  | - Diagnostics and Alarms |  |  |
|  | - Remote Diagnostics, Alarm Notification, Path Trace, Ping, Traceroute | Diagnostic and alarm notification functions, path analysis capabilities |  |
|  | - Redundancy |  |  |
|  | - Redundant Power Supply, Redundant Processor, Fast | Ensuring redundancy for both SDH and MPLS |  |
|  | - Reroute (MPLS), Path Protection (SDH) |  |  |
|  | - Power Requirements |  |  |
|  | - DC 48V, AC 230V | Required power type and voltage |  |
|  | - Environmental Tolerance |  |  |
|  | - Temperature, Humidity, Vibration, Shock | Tolerance to environmental conditions (temperature, humidity, vibration, shock) |  |
|  | - Throughput |  |  |
|  | - Maximum Throughput | Maximum throughput (data transfer capacity) |  |
|  | - Software Upgrades |  |  |
|  | - In-Service Software Upgrades (ISSU), Automated Patching | Software update functionality (ability to update without service interruption) |  |
|  | - Installation and Maintenance |  |  |
|  | - Easy Installation, Low Maintenance Requirement | Easy installation and low maintenance requirements |  |

Here is a summary of the technical particulars and guarantees table for a GPRS modem, similar to the LoRa F8L10 model:

Technical Particulars and Guarantees for GPRS Modem

| No. | Description | NEA Requirement | To be filled by Bidder |
| --- | --- | --- | --- |
| 1 | Modem Model | Equivalent to LoRa F 8L10 |  |
| 2 | Operating Frequency | GSM 900/1800 MHz |  |
| 3 | Communication Protocol | TCP/IP, UDP, HTTP, FTP, SMS |  |
| 4 | Supported Features | POTA (Program Over the Air), SMS Alerts, Auto-restart |  |
| 5 | Interface | RS232, RS485, Ethernet (optional) |  |
| 6 | Communication Speed | Up to 115,200 bps |  |
| 7 | Data Collection | Meter data, instantaneous values, billing data, tamper data |  |
| 8 | Meter Compatibility | Compatible with DLMS/COSEM and IEC 62056 meters |  |
| 9 | GPRS Class | Class 10/12 |  |
| 10 | Power Supply | 48V DC / 110V DC / 230V AC (single/three-phase) |  |
| 11 | Power Consumption | Max 3.5 VA |  |
| 12 | Operating Temperature | -10°C to +55°C |  |
| 13 | Humidity | Up to 95% RH (non-condensing) |  |
| 14 | Enclosure | Polycarbonate, IP55-rated |  |
| 15 | EMI/EMC Compliance | IEC 61000-4-2, 61000-4-4, 61000-4-5 |  |
| 16 | SIM Card Compatibility | 1.8V/3V |  |
| 17 | Antenna Specification | SMA connector, built-in antenna (-6dbi), external antenna option (14dbi) |  |
| 18 | Firmware Update | Over the Air (OTA) |  |
| 19 | Data Transmission Interval | Configurable (15 min, 30 min, 1 hour) |  |
| 20 | Real-Time Alerts | Power, network, communication error alerts |  |
| 21 | Software Tools | Configuration, remote management, firmware update tools |  |
| 22 | Remote Management | Remote reset, configuration change, data collection |  |
| 23 | Security | AES 128/256-bit encryption, VPN support |  |
| 24 | Test Reports | Required EMI/EMC test reports compliant with IEC 61000-4 |  |

Underground Fiber Optic Cable (UGFO) – 24 Fibers

| No. | Description | Unit | NEA requirement | To be filled by Bidder |
| --- | --- | --- | --- | --- |
| 1 | Name of Manufacturer |  |  |  |
| 2 | Country of Origin |  |  |  |
| 3 | Year of Manufacturing Experience | Years | 10 |  |
| 4 | No. of Fibres: Dual Window Single-Mode: | No. | 24 |  |
| 5 | No. of loose Tubes | No. | 6 |  |
| 6 | No. of Fibre / tube | No. | 4 |  |
| 7 | Cable Diameter | Mm | 13.2 |  |
| 8 | Nominal cable weight | Kg/km | 140 |  |
| 9 | Inner sheath thickness | Mm | 1.2 |  |
| 10 | Outer sheath thickness | Mm | 1.6 |  |
| 11 | Expected Cable Life: | Year | 25 Year |  |
| 12 | Whether the offered design(s) of UGFO conforms to the technical specification requirements | - | Yes/No |  |

Underground Fiber Optic Cable (UGFO) – 96 Fibers

| No. | Description | Unit | NEA requirement | To be filled by Bidder |
| --- | --- | --- | --- | --- |
| 1 | Name of Manufacturer |  |  |  |
| 2 | Country of Origin |  |  |  |
| 3 | Year of Manufacturing Experience | Years | 10 |  |
| 4 | No. of Fibres: Dual Window Single-Mode: | No. | 96 |  |
| 5 | No. of loose Tubes | No | 8 |  |
| 6 | No. of Fibre / tube | No | 12 |  |
| 7 | Cable Diameter | Mm | 14.5 |  |
| 8 | Nominal cable weight | kg/km | 175 |  |
| 9 | Inner sheath thickness | Mm | 1.2 |  |
| 10 | Outer sheath thickness | Mm | 1.6 |  |
| 11 | Expected Cable Life: | Year | 25 Year |  |
| 12 | Whether the offered design(s) of UGFO conforms to the technical specification requirements | - | Yes/No |  |

DUAL-WINDOW SINGLE MODE (DW-SM)

| No. | Description | NEA Requirement | To be filled by Bidder |
| --- | --- | --- | --- |
| 1. | Fiber manufacturer(s) / Type: |  |  |
| 2. | Attenuation Coefficient |  |  |
|  | - 1310 nm: | ≤ 0.35 dB/km |  |
|  | - 1550 nm: | ≤ 0.21 dB/km |  |
| 3. | Point discontinuity @ 1310nm: |  |  |
|  | - 1310 nm: | ≤ 0.05 dB |  |
|  | - 1550 nm: | ≤ 0.05 dB |  |
| 4. | Nominal Mode Field Diameter |  |  |
|  | - 1310 nm: | 8.6 to 9.5 µm (± 0.6 µm) |  |
|  | - 1550 nm: | 8.6 to 9.5 µm (± 0.6 µm) |  |
| 5. | Chromatic Dispersion Coefficient |  |  |
|  | - 1310 (1288-1339) nm: | 3.5 ps /(nm x km) |  |
|  | - 1310 (1271-1360) nm: | 5.3 ps/(nm x km) |  |
|  | - 1550 nm: | 18 ps/(nm x km) |  |
| 6. | Zero dispersion wavelength: | 1300 to 1324 nm |  |
| 7. | Cutoff wavelength: | ≤ 1260 nm |  |
| 8. | Bend Performance: |  |  |
|  | - (37.5 mm radius, 100 turns) @1310 nm | ≤ 0.05 dB |  |
|  | - (30 mm radius, 100 turn) @1550 nm | ≤ 0.05 dB |  |
|  | - (16mm radius, 1 turn) @ 1550nm | ≤ 0.05 dB |  |
| 9. | Cladding Diameter (nominal ± deviation): | 125.0 µm ± 1 µm |  |
| 10. | Polarisation mode dispersion coefficient | ≤ 0.2 ps/km1/2 |  |
| 11. | Proof test level | ≥ 0.69 Gpa |  |